### SECTION V.3 TECHNICAL DATA SHEETS

TABLE OF CONTENTS

SECTION V.3 TECHNICAL DATA SHEETS	2

1.	500kV Circuit Breaker	3

2.	500kV Circuit Breaker (TRV= 1.97pu at Isc=20.43kA, RRRV= 0.77 kV/µs.)	9

3.	220kV Circuit Breaker	19

4.	500kV Disconnector and Earthing switch	24

5.	220kV Disconnector and Earthing switch	30

6.	110kV Disconnector and Earthing switch	35

7.	500kv current transformer	40

8.	220kV Current Transformer	42

9.	500kV Capacitor Voltage Transformer	45

10.	220kV Capacitor Voltage Transformer	48

11.	220kV TRV Capacitor	51

12.	110kV TRV Capacitor	54

13.	220kV Current limiting reactor	57

14.	110kV Current limiting reactor	61

15.	35kV Inductive Voltage Transformer	65

16.	500kv surge arrester	68

17.	220kV SURGE ARRESTER	71

19.	500kV Post Insulator	74

20.	220kV Post Insulator	76

21.	110KV POST INSULATOR	78

22.	500kV SUSPENSION AND TENSION INSULATOR	80

23.	220kV Suspension and Tension Insulator	83

24.	110kV Suspension and Tension Insulator	85

25.	All Aluminium Conductor (AAC-1000; AAC-630)	87

26.	HV Connector	89

- SECTION V.3 TECHNICAL DATA SHEETS

- The Data in the “Required” column of the following tables are to be read in conjunction with the descriptions in the technical specifications, and are requirements which the Supplier has to fulfill.

- If there is any deviation from description of equipment and materials item of technical specifications, the data of this item (Data sheets) shall to be used.

- The Bidder shall copy the following data sheets, completely fill in the "Tendered" column, and include them in his Bid. Each data sheet shall be initialled by the Bidder.

- Where the space in the "Tendered" Column is not sufficient to enter Bidder's information, a reference shall be made to separate sheets which are to be attached at the end of the section. Such additional sheets shall contain the specific information and data. References to general leaflets, catalogues etc. are not acceptable and may be evaluated as missing information.

- 500kV Circuit Breaker

| Item No | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 62271-100, IEC 62271-1 |  |
|  | Frequency | Hz | 50 |  |
|  | Method of neutral grounding |  | Directly earthed |  |
|  | Type |  | Outdoor, live tank, single phase (three phases operation), SF6 insulated, single pressure (puffer) type |  |
|  | Nominal voltage | kV | 550 |  |
|  | Max operator voltage | kV | 550 |  |
|  | Rated voltage | kV | ≥ 550 |  |
|  | Rated short-duration power-frequency withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV | 620 800 620 |  |
|  | Rated Lightning impulse (1.2/50µs) withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV peak | 1550 1550(+315) 1550 |  |
|  | Rated switching impulse withstand voltage + Terminal fault + Short-line fault + Out-of-Phase | kV | 1175 900(+450) 1760 |  |
|  | TRV peak values of transient recovery voltage |  |  |  |
|  | TRV for outgoing 500kV Hai Phong – Thai Binh according to IEC 62271-100 and according to the calculation results | pu | 1.97 |  |
|  | TRV for other bays according to IEC 62271-100 | pu | To be specified |  |
|  | Values of prospective transient recovery voltage |  | Required |  |
|  | Test duty T100, T60, T30, T10, OP1-OP2 |  | Theo IEC 62271-100 |  |
|  | + TRV peak value (T100, T60, T30, T10, OP1-OP2) |  | IEC 62271-100 and 13.2 |  |
|  | + Rate-of-rise (T100, T60, T30, T10, OP1-OP2) |  | IEC 62271-100 and 13.2 |  |
|  | Rated normal current | A | ≥ 3150A |  |
|  | Rated short time withstand current | kA rms. | ≥ 50 |  |
|  | Rated duration of short-circuits | sec | ≥ 1 |  |
|  | Rated peak withstand current | kA peak | ≥ 125 |  |
|  | Rated line – charging breaking current | Arms | ≥ 500 |  |
|  | Rate cable – charging breaking current | Arms | 500 |  |
|  | Rated capacitive breaking current | Arms | 400 |  |
|  | % DC component of short-circuit breaking current |  | To be specified |  |
|  | Resistance of main contact (new contact) | µΩ | To be specified |  |
|  | Operating mechanism drive type |  | Spring (There is a charge indicator, both manual and motor) |  |
|  | Maximum noise level according to IEC62271-37-082 when the circuit breaker is in operation | dB | To be specified |  |
|  | On/Off Indicator |  | Yes |  |
|  | Operating mechanism |  | Single pole |  |
|  | Manufacturer’s name |  | To be specified |  |
|  | Country of origin |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Mechanical operation duration | Times | 10,000 |  |
|  | Number of times of switching (closing-opening) of rated current | Times | 2500 |  |
|  | Number of operation with short circuit current is 50% of rating | Times | 30 |  |
|  | Number of operation with short circuit current is 100% of rating | Times | 10 |  |
|  | Opening time | ms | ≤ 40 |  |
|  | Closing time | ms | ≤120 |  |
|  | Open-close time of 3 phases not simultaneously | ms | ≤4 |  |
|  | Rated Operating Sequence |  | O-0.3sec.-CO -3min -CO |  |
|  | Minimum Clearance: |  |  |  |
|  | Between phases | mm | ≥ 7400 |  |
|  | Between phase and earth | mm | ≥ 4100 |  |
|  | Porcelain insulator: |  |  |  |
|  | - Applicable standard |  | According to IEC 62155 or equivalent |  |
|  | - Material |  | Brown porcelain |  |
|  | - Minimum nominal creepage distance | mm/kV | 25 |  |
|  | - Total creepage distance | mm | To be specified |  |
|  | Maximum impact load when the circuit breaker is in operation, kN | kN | To be specified |  |
|  | Circuit Breaker terminal load capacity, kN | kN | To be specified |  |
|  | Chamber system, bushing: |  |  |  |
| - | There is a dehumidifier, decomposition product and pressure release unit rising inside |  | Comply |  |
| - | Links between the pole or other parts with bolts |  | Comply |  |
|  | There is an corona ring to ensure the voltage balance between pole |  | yes |  |
|  | Interrupting and arcing chamber |  |  |  |
|  | Structure of the Interrupting and arcing chamber |  | live tank |  |
|  | Quantity of interrupting chamber per one pole. |  | ≥02 |  |
|  | First-pole-to-clear factor | pu | 1.3 |  |
|  | Terminal fault Short-line fault Out-of-phase reverse fault |  | 1.3 1 2 |  |
|  | Insulating medium |  | SF6 |  |
|  | Grading capacitor (is installed parallel with chamber) |  | yes |  |
|  | Quantity of Grading capacitor per one pole |  | ≥2 |  |
|  | Closing resistor | Ohm | N/A |  |
|  | Number of closing coil |  | 1 coil/phase |  |
|  | Number of tripping coil |  | 2 coil /phase |  |
|  | Number of auxiliary contacts for 1 phase |  |  |  |
|  | Normally opened |  | 12 NO |  |
|  | Normally closed |  | 12 NC |  |
|  | SF6 gas |  |  |  |
|  | The meter indicates gas density |  | - Temperature compensation type - 03 meter for 3 phases. Gas alarm circuit level 1 (alarm), level 2 (alarm and operating lock) |  |
|  | One way valve for charge (discharge) SF6 |  | Yes |  |
|  | Leakage of SF6 per year | %/year | ≤ 0.5 |  |
|  | Purity of SF6 | % | ≥ 98,5% V |  |
|  | Dew-point temperature | oC | Comply with IEC 60376 |  |
|  | SF6 mass for one three-pole circuit breaker | kg | To be specified |  |
|  | Rated SF6 density | kg/m3 | To be specified |  |
|  | Threshold gas density SF 6 level 1 | kg/m3 | To be specified |  |
|  | Threshold gas density SF 6 level 2 | kg/m3 | To be specified |  |
|  | Local control cabinet: |  |  |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Material of cabinet |  | Aluminium alloy or stainless steel |  |
|  | Protection class |  | IP55 |  |
|  | Minimum thickness of cabinet, mm |  | ≥2 |  |
|  | Full device and accessories for operational in “local” and “remote” mode |  | Yes |  |
|  | Mechanical opening/ closing operations |  | Yes |  |
|  | Operating counter |  | Yes |  |
|  | Other functions circuit (trip coil supervision circuit, power state of circuit, springs charged circuit…) |  | Yes |  |
|  | Anti-pumping circuit |  | Yes |  |
|  | Non-synchronous protection circuit |  | Yes |  |
|  | Overcurrent and overload protection circuit for the motor |  | Yes |  |
|  | Spring charge indicator |  | Yes |  |
|  | System heating and lighting with LED lights, MCB |  | Yes |  |
|  | Spring charge |  | Spring charge (Motor and manual drive) |  |
|  | Maximum spring charge time | s | 15 |  |
|  | Steel supporting structure |  |  |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Material |  | Hot dip galvanized |  |
|  | Auxiliary supply voltage: |  |  |  |
|  | Motor Recommend using an additional 220 VAC source: 220 (+10%; -15%) | VDC and VAC | 220 (+10%; -15%) |  |
|  | Trip coil | VDC | 220 (+10%; -30%) |  |
|  | Close coil | VDC | 220 (+10%; -25%) |  |
|  | Heating and Lighting | VAC | 220 (+10%; -15%) |  |
|  | Maximum power trip coil or close coil for all 3 phases | VA | 1200 |  |
|  | HV terminal: |  |  |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Materials |  | Aluminum alloy |  |
|  | Dimensions |  | To be specified |  |
|  | Number of holes |  | To be specified |  |
|  | Size of holes |  | To be specified |  |
|  | Spacing of holes |  | To be specified |  |
|  | Bolts |  | Stainless Steel |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 1677/QĐ-EVNNPT, (EVNNPT) |  | Yes |  |

- 500kV Circuit Breaker (TRV= 1.97pu at Isc=20.43kA, RRRV= 0.77 kV/µs.)

| Item No | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 62271-100, IEC 62271-1 |  |
|  | Frequency | Hz | 50 |  |
|  | Method of neutral grounding |  | Directly earthed |  |
|  | Type |  | Outdoor, live tank, single phase (three phases operation), SF6 insulated, single pressure (puffer) type |  |
|  | Nominal voltage | kV | 550 |  |
|  | Max operator voltage | kV | 550 |  |
|  | Rated voltage | kV | ≥ 550 |  |
|  | Rated short-duration power-frequency withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV | 620 800 620 |  |
|  | Rated Lightning impulse (1.2/50µs) withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV peak | 1550 1550(+315) 1550 |  |
|  | Rated switching impulse withstand voltage + Terminal fault + Short-line fault + Out-of-Phase | kV | 1175 900(+450) 1760 |  |
|  | TRV peak values of transient recovery voltage |  |  |  |
|  | TRV for outgoing 500kV Hai Phong – Thai Binh according to IEC 62271-100 and according to the calculation results | pu | 1.97 |  |
|  | TRV for other bays according to IEC 62271-100 | pu | To be specified |  |
|  | Values of prospective transient recovery voltage |  | Required |  |
|  | Test duty T100, T60, T30, T10, OP1-OP2 |  | Theo IEC 62271-100 |  |
|  | + TRV peak value (T100, T60, T30, T10, OP1-OP2) |  | IEC 62271-100 and 13.2 |  |
|  | + Rate-of-rise (T100, T60, T30, T10, OP1-OP2) |  | IEC 62271-100 and 13.2 |  |
|  | Provide tests or proving of the below parameters that must be met |  | Required |  |
|  | + TRV peak value at short-circuit current Isc=20.43kA, RRRV= 0.77 kV/µs. |  | 1.97 p.u |  |
|  | Rated normal current | A | ≥ 3150A |  |
|  | Rated short time withstand current | kA rms. | ≥ 50 |  |
|  | Rated duration of short-circuits | sec | ≥ 1 |  |
|  | Rated peak withstand current | kA peak | ≥ 125 |  |
|  | Rated line – charging breaking current | Arms | ≥ 500 |  |
|  | Rate cable – charging breaking current | Arms | 500 |  |
|  | Rated capacitive breaking current | Arms | 400 |  |
|  | % DC component of short-circuit breaking current |  | To be specified |  |
|  | Resistance of main contact (new contact) | µΩ | To be specified |  |
|  | Operating mechanism drive type |  | Spring (There is a charge indicator, both manual and motor) |  |
|  | Maximum noise level according to IEC62271-37-082 when the circuit breaker is in operation | dB | To be specified |  |
|  | On/Off Indicator |  | Yes |  |
|  | Operating mechanism |  | Single pole |  |
|  | Manufacturer’s name |  | To be specified |  |
|  | Country of origin |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Mechanical operation duration | Times | 10,000 |  |
|  | Number of times of switching (closing-opening) of rated current | Times | 2500 |  |
|  | Number of operation with short circuit current is 50% of rating | Times | 30 |  |
|  | Number of operation with short circuit current is 100% of rating | Times | 10 |  |
|  | Opening time | ms | ≤ 40 |  |
|  | Closing time | ms | ≤120 |  |
|  | Open-close time of 3 phases not simultaneously | ms | ≤4 |  |
|  | Rated Operating Sequence |  | O-0.3sec.-CO -3min -CO |  |
|  | Minimum Clearance: |  |  |  |
|  | Between phases | mm | ≥ 7400 |  |
|  | Between phase and earth | mm | ≥ 4100 |  |
|  | Porcelain insulator: |  |  |  |
|  | - Applicable standard |  | According to IEC 62155 or equivalent |  |
|  | - Material |  | Brown porcelain |  |
|  | - Minimum nominal creepage distance | mm/kV | 25 |  |
|  | - Total creepage distance | mm | To be specified |  |
|  | Maximum impact load when the circuit breaker is in operation, kN | kN | To be specified |  |
|  | Circuit Breaker terminal load capacity, kN | kN | To be specified |  |
|  | Chamber system, bushing: |  |  |  |
| - | There is a dehumidifier, decomposition product and pressure release unit rising inside |  | Comply |  |
| - | Links between the pole or other parts with bolts |  | Comply |  |
|  | There is an corona ring to ensure the voltage balance between pole |  | yes |  |
|  | Interrupting and arcing chamber |  |  |  |
|  | Structure of the Interrupting and arcing chamber |  | live tank |  |
|  | Quantity of interrupting chamber per one pole. |  | ≥02 |  |
|  | First-pole-to-clear factor | pu | 1.3 |  |
|  | Terminal fault Short-line fault Out-of-phase reverse fault |  | 1.3 1 2 |  |
|  | Insulating medium |  | SF6 |  |
|  | Grading capacitor (is installed parallel with chamber) |  | yes |  |
|  | Quantity of Grading capacitor per one pole |  | ≥2 |  |
|  | Closing resistor | Ohm | N/A |  |
|  | Number of closing coil |  | 1 coil/phase |  |
|  | Number of tripping coil |  | 2 coil /phase |  |
|  | Number of auxiliary contacts for 1 phase |  |  |  |
|  | Normally opened |  | 12 NO |  |
|  | Normally closed |  | 12 NC |  |
|  | SF6 gas |  |  |  |
|  | The meter indicates gas density |  | - Temperature compensation type - 03 meter for 3 phases. Gas alarm circuit level 1 (alarm), level 2 (alarm and operating lock) |  |
|  | One way valve for charge (discharge) SF6 |  | Yes |  |
|  | Leakage of SF6 per year | %/year | ≤ 0.5 |  |
|  | Purity of SF6 | % | ≥ 98,5% V |  |
|  | Dew-point temperature | oC | Comply with IEC 60376 |  |
|  | SF6 mass for one three-pole circuit breaker | kg | To be specified |  |
|  | Rated SF6 density | kg/m3 | To be specified |  |
|  | Threshold gas density SF 6 level 1 | kg/m3 | To be specified |  |
|  | Threshold gas density SF 6 level 2 | kg/m3 | To be specified |  |
|  | Local control cabinet: |  |  |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Material of cabinet |  | Aluminium alloy or stainless steel |  |
|  | Protection class |  | IP55 |  |
|  | Minimum thickness of cabinet, mm |  | ≥2 |  |
|  | Full device and accessories for operational in “local” and “remote” mode |  | Yes |  |
|  | Mechanical opening/ closing operations |  | Yes |  |
|  | Operating counter |  | Yes |  |
|  | Other functions circuit (trip coil supervision circuit, power state of circuit, springs charged circuit…) |  | Yes |  |
|  | Anti-pumping circuit |  | Yes |  |
|  | Non-synchronous protection circuit |  | Yes |  |
|  | Overcurrent and overload protection circuit for the motor |  | Yes |  |
|  | Spring charge indicator |  | Yes |  |
|  | System heating and lighting with LED lights, MCB |  | Yes |  |
|  | Spring charge |  | Spring charge (Motor and manual drive) |  |
|  | Maximum spring charge time | s | 15 |  |
|  | Steel supporting structure |  |  |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Material |  | Hot dip galvanized |  |
|  | Auxiliary supply voltage: |  |  |  |
|  | Motor Recommend using an additional 220 VAC source: 220 (+10%; -15%) | VDC and VAC | 220 (+10%; -15%) |  |
|  | Trip coil | VDC | 220 (+10%; -30%) |  |
|  | Close coil | VDC | 220 (+10%; -25%) |  |
|  | Heating and Lighting | VAC | 220 (+10%; -15%) |  |
|  | Maximum power trip coil or close coil for all 3 phases | VA | 1200 |  |
|  | HV terminal: |  |  |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Materials |  | Aluminum alloy |  |
|  | Dimensions |  | To be specified |  |
|  | Number of holes |  | To be specified |  |
|  | Size of holes |  | To be specified |  |
|  | Spacing of holes |  | To be specified |  |
|  | Bolts |  | Stainless Steel |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 1677/QĐ-EVNNPT, (EVNNPT) |  | Yes |  |

| Values of prospective transient recovery voltage (FOR THAI BINH OUTGOING BAYS) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rated voltage | Test duty | First-pole-to-clear factor | Amplitude factor | First reference voltage | Time | TRV peak value | Time | Time delay | Voltage | Time | Rate of rise | Type test certificates for reference |  |
| Ur (kV) |  | kpp (p.u) | kaf (p.u) | u1(kV) | t1(ms) | uc(kV) | t2 or t3 (ms) | td(ms) | u'(kV) | t'(ms) | u1/t1 uc/t3 (kV/ms) |  |  |
| 550 | T100 |  |  |  |  |  |  |  |  |  |  |  |  |
|  | T60 |  |  |  |  |  |  |  |  |  |  |  |  |
|  | T30 |  |  |  |  |  |  |  |  |  |  |  |  |
|  | T10 |  |  |  |  |  |  |  |  |  |  |  |  |

Notes:

- The Bidder shall supply test report (or type test) to prove above values

- The Bidder must offer all of above parameters.

| Values of transient recovery voltage (FOR THAI BINH OUTGOING BAYS) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rated voltage | Test duty | First-pole-to-clear factor | Amplitude factor | First reference voltage | Time | TRV peak value | Time | Time delay | Voltage | Time | Rate of rise of recovery voltage | Type test certificates for reference |  |
| Ur (kV) |  | kpp (p.u) | kaf (p.u) | u1(kV) | t1(ms) | uc(kV) | t2 or t3 (ms) | td(ms) | u'(kV) | t'(ms) | u1/t1 (kV/ms) |  |  |
| 550 | Terminal fault |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Short-line fault |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Out-of-phase |  |  |  |  |  |  |  |  |  |  |  |  |

Notes:

- The Bidder shall supply test report (or type test) to prove above values

- The Bidder must offer all of above parameters.

| Values of prospective transient recovery voltage (FOR OTHER BAYS) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rated voltage | Test duty | First-pole-to-clear factor | Amplitude factor | First reference voltage | Time | TRV peak value | Time | Time delay | Voltage | Time | Rate of rise | Type test certificates for reference |  |
| Ur (kV) |  | kpp (p.u) | kaf (p.u) | u1(kV) | t1(ms) | uc(kV) | t2 or t3 (ms) | td(ms) | u'(kV) | t'(ms) | u1/t1 uc/t3 (kV/ms) |  |  |
| 550 | T100 |  |  |  |  |  |  |  |  |  |  |  |  |
|  | T60 |  |  |  |  |  |  |  |  |  |  |  |  |
|  | T30 |  |  |  |  |  |  |  |  |  |  |  |  |
|  | T10 |  |  |  |  |  |  |  |  |  |  |  |  |

Notes:

- The Bidder shall supply test report (or type test) to prove above values

- The Bidder must offer all of above parameters.

| Values of transient recovery voltage (FOR OTHER BAYS) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rated voltage | Test duty | First-pole-to-clear factor | Amplitude factor | First reference voltage | Time | TRV peak value | Time | Time delay | Voltage | Time | Rate of rise of recovery voltage | Type test certificates for reference |  |
| Ur (kV) |  | kpp (p.u) | kaf (p.u) | u1(kV) | t1(ms) | uc(kV) | t2 or t3 (ms) | td(ms) | u'(kV) | t'(ms) | u1/t1 (kV/ms) |  |  |
| 550 | Terminal fault |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Short-line fault |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Out-of-phase |  |  |  |  |  |  |  |  |  |  |  |  |

Notes:

- The Bidder shall supply test report (or type test) to prove above values

- The Bidder must offer all of above parameters.

220kV Circuit Breaker

| Item No | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Model type |  | To be specified |  |
|  | Applicable standard |  | IEC 62271-100, IEC 62271-1 |  |
|  | Frequency | Hz | 50 |  |
|  | Method of neutral grounding |  | Directly earthed |  |
|  | Type |  | Outdoor, live tank, single phase (three phases operation), SF6 insulated, single pressure (puffer) type |  |
|  | Nominal voltage | kV | 220 |  |
|  | Max operator voltage | kV | ≥242 |  |
|  | Rated voltage | kV | ≥ 245 |  |
|  | Rated short-duration power-frequency withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV | 460 |  |
|  | Rated Lightning impulse (1.2/50µs) withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV peak | 1050 |  |
|  | TRV peak values of transient recovery voltage, kV + Terminal fault + Short-line fault + Out-of-Phase | kV | 364 280 500 |  |
|  | Rated current |  |  |  |
| - | AT1, AT2 transformer | A | 3150 |  |
| - | outgoing bays | A | 2000 |  |
|  | Rated short-time withstand current | kA rms. | ≥ 50 |  |
|  | Rated duration of short-circuits | sec | ≥ 1 |  |
|  | Rated peak withstand current | kA peak | ≥ 125 |  |
|  | Rated line – charging breaking current | Arms | ≥ 125 |  |
|  | Rate cable – charging breaking current | Arms | 250 |  |
|  | Rated capacitive breaking current | Arms | 400 |  |
|  | % DC component of short-circuit breaking current |  | To be specified |  |
|  | Resistance of main contact | µΩ | To be specified |  |
|  | Operating mechanism drive type |  | Spring (There is a charge indicator, both manual and motor) |  |
|  | Maximum noise level according to IEC62271-37-082 when the circuit breaker is in operation | dB | To be specified |  |
|  | On/Off Indicator |  | Yes |  |
|  | Operating mechanism |  | Single pole |  |
|  | Manufacturer’s name |  | To be specified |  |
|  | Country of origin |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Mechanical operation duration | Times | 10,000 |  |
|  | Number of operation at 100% rated current | Times | 2500 |  |
|  | Number of operation with short circuit current is 50% of rating | Times | 30 |  |
|  | Number of operation with short circuit current is 100% of rating | Times | 10 |  |
|  | Opening time | ms | ≤ 35 |  |
|  | Closing time | ms | ≤70 |  |
|  | Open-close time of 3 phases not simultaneously | ms | ≤4 |  |
|  | Rated Operating Sequence |  | O-0.3sec.-CO -3min -CO |  |
|  | Minimum Clearance: |  |  |  |
|  | Between phases | mm | ≥ 2100 |  |
|  | Between phase and earth | mm | ≥ 2100 |  |
|  | Porcelain insulator: |  |  |  |
|  | - Applicable standard |  | According to IEC 62155 or equivalent |  |
|  | - Material |  | Brown porcelain |  |
|  | - Minimum nominal creepage distance | mm/kV | 25 |  |
|  | - Total creepage distance | mm | To be specified |  |
|  | Maximum impact load when the circuit breaker is in operation, kN | kN | To be specified |  |
|  | Circuit Breaker terminal load capacity, kN | kN | To be specified |  |
|  | Chamber system, bushing: |  |  |  |
| - | There is a dehumidifier, decomposition product and pressure release unit rising inside |  | Comply |  |
| - | Links between the pole or other parts with bolts |  | Comply |  |
|  | Interrupting and arcing chamber |  |  |  |
|  | Structure of the Interrupting and arcing chamber |  | live tank |  |
|  | Quantity of interrupting chamber per one pole. |  | 01 |  |
|  | First-pole-to-clear factor | pu | 1.3 |  |
|  | Terminal fault Short-line fault Out-of-phase reverse fault |  | 1,3 1 2 |  |
|  | Insulating medium |  | SF6 |  |
|  | Number of closing coil |  | 1 coil/phase |  |
|  | Number of tripping coil |  | 2 coil /phase |  |
|  | Number of auxiliary contacts for 1 phase |  |  |  |
|  | Normally opened |  | 12 NO |  |
|  | Normally closed |  | 12 NC |  |
|  | SF6 gas |  |  |  |
|  | The meter indicates gas density |  | - Temperature compensation type - 03 meter for 3 phases. Gas alarm circuit level 1 (alarm), level 2 (alarm and operating lock) |  |
|  | One way valve for charge (discharge) SF6 |  | Yes |  |
|  | Leakage of SF6 per year | %/year | ≤ 0.5 |  |
|  | Purity of SF6 | % | ≥ 98,5% V |  |
|  | Dew-point temperature | oC | Comply with IEC 60376 |  |
|  | SF6 mass for one three-pole circuit breaker | kg | To be specified |  |
|  | Rated SF6 density | kg/m3 | To be specified |  |
|  | Threshold gas density SF 6 level 1 | kg/m3 | To be specified |  |
|  | Threshold gas density SF 6 level 2 | kg/m3 | To be specified |  |
|  | Local control cabinet: |  |  |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Material of cabinet |  | Aluminium alloy or stainless steel |  |
|  | Protection class |  | IP55 |  |
|  | Minimum thickness of cabinet, mm |  | ≥2 |  |
|  | Full device and accessories for operational in “local” and “remote” mode |  | Yes |  |
|  | Mechanical opening/ closing operations |  | Yes |  |
|  | Operating counter |  | Yes |  |
|  | Other functions circuit (trip coil supervision circuit, power state of circuit, springs charged circuit…) |  | Yes |  |
|  | Anti-pumping circuit |  | Yes |  |
|  | Non-synchronous protection circuit |  | Yes |  |
|  | Overcurrent and overload protection circuit for the motor |  | Yes |  |
|  | Spring charge indicator |  | Yes |  |
|  | System heating and lighting with LED lights, MCB |  | Yes |  |
|  | Spring charge |  | Spring charge (Motor and manual drive) |  |
|  | Maximum spring charge time | s | 15 |  |
|  | Steel supporting structure |  |  |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Material |  | Hot dip galvanized |  |
|  | Auxiliary supply voltage: |  |  |  |
|  | Motor Recommend using an additional 220 VAC source: 220 (+10%; -15%) | VDC and VAC | 220 (+10%; -15%) |  |
|  | Trip coil | VDC | 220 (+10%; -30%) |  |
|  | Close coil | VDC | 220 (+10%; -25%) |  |
|  | Heating and Lighting | VAC | 220 (+10%; -15%) |  |
|  | Maximum power trip coil or close coil for all 3 phases | VA | 1200 |  |
|  | HV terminal: |  |  |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Materials |  | Aluminum alloy |  |
|  | Dimensions |  | To be specified |  |
|  | Number of holes |  | To be specified |  |
|  | Size of holes |  | To be specified |  |
|  | Spacing of holes |  | To be specified |  |
|  | Bolts |  | Stainless Steel |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 1676/QĐ-EVNNPT; 272/QĐ-EVN (EVN) |  | Yes |  |

500kV Disconnector and Earthing switch

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
| 1.1 | Manufacturer/Country of Origin |  | To be specified |  |
| 1.2 | Model type |  | To be specified |  |
| 1.3 | Applicable standard |  | IEC 62271-102 |  |
| 2 | Rated frequency, Hz |  | 50 |  |
| 3 | Method of neutral grounding |  | Directly earthed |  |
| 4 | Type |  | outdoor |  |
| 4.1 | Structure of one set |  | single phase/three phase |  |
| 4.2 | Break type |  | Vertical break, knee type |  |
| 4.2 | Number of earthing switches can be equipped for disconnector |  | (0, 1, 2) earthing blade |  |
| 5 | Voltage parameters |  |  |  |
| 5.1 | System voltage | kV | 500 |  |
| 5.2 | Maximum voltage | kV | ≥550 |  |
| 5.3 | Rated voltage | kV | ≥550 |  |
| 5.4 | Rated short-duration power-frequency withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV | ≥620 ≥800 ≥620 |  |
| 5.5 | Rated lightning impulse withstand voltage (1,2/50 µs-BIL) + Phase-to-Earth + Across the isolating distance + Between phases | kV peak | ≥1550 ≥1550 (+315) ≥1550 |  |
| 5.6 | Rated switching impulse voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV peak | ≥1175 ≥900 (+450) ≥1760 |  |
| 6 | Current parameters |  |  |  |
| 6.1 | Rated normal current Ir | A | ≥ 3150 |  |
| 6.2 | Rated short-time withstand current | kA rms | ≥50 |  |
| 6.3 | Rated duration of short-circuit | s | ≥1 |  |
| 6.4 | Rated peak withstand current | kA peak | ≥125 |  |
| 7 | Main circuit contact resistance | µΩ | To be specified |  |
| 8 | Earthing switch parameters |  |  |  |
| 8.1 | Rated short-circuit making current | kA | ≥50 |  |
| 8.2 | Rated induced current of electrostatic coupling | A rms | ≥25 (applied for ES of transmission line side at outgoing bays) |  |
| 8.3 | Rated induced current of electromagnetic coupling | A rms | 160 (applied for ES of transmission line side at outgoing bays) |  |
| 8.4 | Rated withstand voltage between insulated terminals and bases earthed | kV | ≥635 |  |
| 9 | Operational capabilities of disconnector, earthing switch |  |  |  |
| 9.1 | Drive mechanism |  | Single phase/ three phase |  |
| 9.2 | Mechanical endurance class |  |  |  |
| - | Disconnector |  | M1 |  |
| - | Earthing switch |  | M0 |  |
| 9.3 | Total mechanical operating, no maintenance |  |  |  |
| - | Disconnector | times | ≥2000 |  |
| - | Earthing switch | times | ≥1000 |  |
| 9.4 | Operated lever |  | yes |  |
| 9.5 | Mechanical interlock (Disconnector and Earthing switch) |  | yes |  |
| 10 | Total weight | kg | To be specified |  |
| 11 | Required clearance |  |  |  |
| 11.1 | Phase to phase | mm | ≥ 6100 (or switching impulse response 1760 kV peak) |  |
| 11.2 | Phase to earth | mm | ≥ 4100 (or switching impulse response 1175 kV peak) |  |
| 12 | Poles post of disconnector |  |  |  |
| 12.1 | Applicable standard |  | IEC 60273 or equivalent |  |
| 12.2 | Material |  | Brown ceramic porcelain |  |
| 12.3 | Minimum creepage distance | mm/ kV | ≥25 |  |
| 12.4 | Total creepage distance | mm | To be specified |  |
| 12.5 | Withstand the impact loads of disconnector - Three phase disconnector/Earthing switch + Straight load Fa1, Fa2, kN + Cross load Fb1, Fb2, kN - Single phase disconnector/Earthing switch + Straight load Fa1, Fa2, kN + Cross load Fb1, Fb2, kN - Vertical Force, Fc - Vertical Force, Fc, kN | kN | 1.6: Ir≤3150A 2.0: Ir>3150A 0.53: Ir≤3150A 0.66: Ir>3150A 2.0: Ir≤3150A 4.0: Ir>3150A 0.8: Ir≤3150A 1.6: Ir>3150A 1.5 |  |
| 12.6 | Maximum impact load when the disconnector operates | kN | To be specified |  |
| 12.7 | Minimum distance in static condition: - Between phase and earth | mm | 4100 |  |
|  | - Between phases, mm | mm | 4100 |  |
| 13 | Material of main contact |  | Copper, Copper alloy or silver/nickel plated aluminum alloy |  |
| 14 | Operating mechanism |  |  |  |
| 14.1 | Disconnector |  | Manual and/or electrical motor |  |
| 14.2 | Earthing switch |  | Manual and/or electrical motor |  |
| 15 | Local control cabinet of disconnector, earthing switch: |  |  |  |
| 15.1 | Cabinet enclosure material |  | Aluminum alloy or stainless steel (Inox 304) or galvanized steel and the cabinet surface can be painted suitable to requirements |  |
| 15.2 | Minimum protection class |  | IP55 |  |
| 15.3 | Minimum thickness of cabinet enclosure | mm | ≥2 |  |
| 15.4 | Limit switch contact of disconnector |  | ≥(3NO+3NC) |  |
| 15.5 | Auxiliary switch contact of disconnector |  | ≥(12NO+12NC) |  |
| 15.6 | Auxiliary switch contact of earthing switch |  | ≥(10NO+10NC) |  |
| 15.7 | Rated DC current of the auxiliary contact | A | 10 |  |
| 15.8 | DC current withstands short-time of the auxiliary contact |  | 100 A/30 ms |  |
| 15.9 | Selection switch of Local/Remote |  | yes |  |
| 15.10 | "Open/Close" push buttons of disconnector, earthing switch |  | yes |  |
| 15.11 | Motor and MCBs with auxiliary contacts have separate power supply |  | yes |  |
| 15.12 | Overcurrent and overload protection for the motor |  | yes |  |
| 15.13 | Drying system with temperature sensor, led lighting, drying and lighting have separate power supply by MCBs with auxiliary contacts |  | yes |  |
| 15.14 | Electrical interlock circuit between disconnector and earthing switch |  | yes |  |
| 16 | Supply voltage: |  |  |  |
| 16.1 | Motor | VDC | 220 (+10%; -15%) |  |
| 16.2 | Trip and Close | VDC | 220 (+10%; -15%) |  |
| 16.3 | Heating and Lighting | VAC | 220 (+10%; -15%) |  |
| 17 | Material of support structures for disconnector |  | Galvanized steel |  |
| 18 | HV terminals: |  |  |  |
| 18.1 | Materials |  | Aluminum alloy /copper |  |
| 18.2 | Dimensions |  | suitable for conductor |  |
| 18.3 | Bolt |  | Stainless steel |  |
| 19 | Catalogues |  | To be supplied |  |
| 20 | Requirements for testing (according to Technical Specification) |  | Yes |  |
| 21 | The remaining parameters or different will comply with the provisions of 1676/QĐ-EVNNPT (EVNNPT) |  | Yes |  |

220kV Disconnector and Earthing switch

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
| 1.1 | Manufacturer/Country of Origin |  | To be specified |  |
| 1.2 | Model type |  | To be specified |  |
| 1.3 | Applicable standard |  | IEC 62271-102 |  |
| 2 | Rated frequency, Hz |  | 50 |  |
| 3 | Method of neutral grounding |  | Directly earthed |  |
| 4 | Type |  | outdoor |  |
| 4.1 | Structure of one set |  | single phase/three phase |  |
| 4.2 | Break type |  | horizontal break |  |
| 4.2 | Number of earthing switches can be equipped for disconnector |  | (0, 1, 2) earthing blade |  |
| 5 | Voltage parameters |  |  |  |
| 5.1 | System voltage | kV | 220 |  |
| 5.2 | Maximum voltage | kV | ≥242 |  |
| 5.3 | Rated voltage | kV | ≥245 |  |
| 5.4 | Rated short-duration power-frequency withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV | ≥460 ≥530 |  |
| 5.5 | Rated lightning impulse withstand voltage (1,2/50 µs-BIL) + Phase-to-Earth + Across the isolating distance + Between phases | kV peak | ≥1050 ≥1200 |  |
| 6 | Current parameters |  |  |  |
| 6.1 | Rated normal current Ir | A | ≥ 3150 (transformer) 2000A (outgoing bays) |  |
| 6.2 | Rated short-time withstand current | kA rms | ≥50 |  |
| 6.3 | Rated duration of short-circuit | s | ≥1 |  |
| 6.4 | Rated peak withstand current | kA peak | ≥125 |  |
| 7 | Main circuit contact resistance | µΩ | To be specified |  |
| 8 | Earthing switch parameters |  |  |  |
| 8.1 | Rated short-circuit making current | kA | 50 |  |
| 8.2 | Rated induced current of electrostatic coupling | A rms | 3 |  |
| 8.3 | Rated induced current of electromagnetic coupling Rated induced current of electromagnectic coupling | A rms | ≥80 |  |
| 8.4 | Rated withstand voltage between insulated terminals and bases earthed | kV | ≥283 |  |
| 9 | Operational capabilities of disconnector, earthing switch |  |  |  |
| 9.1 | Drive mechanism |  | Single phase/ three phase |  |
| 9.2 | Mechanical endurance class |  |  |  |
| - | Disconnector |  | M1 |  |
| - | Earthing switch |  | M0 |  |
| 9.3 | Total mechanical operating, no maintenance |  |  |  |
| - | Disconnector | times | ≥2000 |  |
| - | Earthing switch | times | ≥1000 |  |
| 9.4 | Operated lever |  | yes |  |
| 9.5 | Mechanical interlock (Disconnector and Earthing switch) |  | yes |  |
| 10 | Total weight | kg | To be specified |  |
| 11 | Required clearance |  |  |  |
| 11.1 | Phase to phase | mm | ≥ 2100 |  |
| 11.2 | Phase to earth | mm | ≥ 2100 |  |
| 12 | Poles post of disconnector |  |  |  |
| 12.1 | Applicable standard |  | IEC 60273 or equivalent |  |
| 12.2 | Material |  | Brown ceramic porcelain |  |
| 12.3 | Minimum creepage distance | mm/ kV | ≥25 |  |
| 12.4 | Total creepage distance | mm | To be specified |  |
| 12.5 | Withstand the impact loads of disconnector - Three phase disconnector/Earthing switch + Straight load Fa1, Fa2, kN + Cross load Fb1, Fb2, kN - Single phase disconnector/Earthing switch + Straight load Fa1, Fa2, kN + Cross load Fb1, Fb2, kN - Vertical Force, Fc, kN | kN | 0.8: Ir≤2500A 1.0: Ir>2500A 0.27: Ir≤2500A 0.33:Ir>2500A 1.25: Ir≤2500A 1.6: Ir>2500A 0.4: Ir≤2500A 0.5: Ir>2500A 1.25 |  |
| 12.6 | Maximum impact load when the disconnector operates | kN | To be specified |  |
| 12.7 | Minimum distance in static condition: - Between phase and earth | mm | ≥2100 |  |
|  | - Between two poles/phase | mm | ≥2100 and ≤ 2600 (suitable for installation in 220kV bays) |  |
| 13 | Material of main contact |  | Copper, Copper alloy or silver/nickel plated aluminum alloy |  |
| 14 | Operating mechanism |  |  |  |
| 14.1 | Disconnector |  | Manual and/or electrical motor |  |
| 14.2 | Earthing switch |  | Manual and/or electrical motor |  |
| 15 | Local control cabinet of disconnector, earthing switch: |  |  |  |
| 15.1 | Cabinet enclosure material |  | Aluminum alloy or stainless steel (Inox 304) or galvanized steel and the cabinet surface can be painted suitable to requirements |  |
| 15.2 | Minimum protection class |  | IP55 |  |
| 15.3 | Minimum thickness of cabinet enclosure | mm | ≥2 |  |
| 15.4 | Limit switch contact of disconnector |  | ≥(2NO+2NC) |  |
| 15.5 | Auxiliary switch contact of disconnector |  | ≥(12NO+12NC) |  |
| 15.6 | Auxiliary switch contact of earthing switch |  | ≥(8NO+8NC) |  |
| 15.7 | Rated DC current of the auxiliary contact | A | 10 |  |
| 15.8 | DC current withstands short-time of the auxiliary contact |  | 100 A/30 ms |  |
| 15.9 | Selection switch of Local/Remote |  | yes |  |
| 15.10 | "Open/Close" push buttons of disconnector, earthing switch |  | yes |  |
| 15.11 | Motor and MCBs with auxiliary contacts have separate power supply |  | yes |  |
| 15.12 | Overcurrent and overload protection for the motor |  | yes |  |
| 15.13 | Drying system with temperature sensor, led lighting, drying and lighting have separate power supply by MCBs with auxiliary contacts |  | yes |  |
| 15.14 | Electrical interlock circuit between disconnector and earthing switch |  | yes |  |
| 16 | Supply voltage: |  |  |  |
| 16.1 | Motor | VDC | 220 (+10%; -15%) |  |
| 16.2 | Trip and Close | VDC | 220 (+10%; -15%) |  |
| 16.3 | Heating and Lighting | VAC | 220 (+10%; -15%) |  |
| 17 | Material of support structures for disconnector |  | Galvanized steel |  |
| 18 | HV terminals: |  |  |  |
| 18.1 | Materials |  | Aluminum alloy /copper |  |
| 18.2 | Dimensions |  | suitable for conductor |  |
| 18.3 | Bolt |  | Stainless steel |  |
| 19 | Catalogues |  | To be supplied |  |
| 20 | Requirements for testing (according to Technical Specification) |  | Yes |  |
| 21 | The remaining parameters or different will comply with the provisions of 1676/QĐ-EVNNPT (EVNNPT) |  | Yes |  |

110kV Disconnector and Earthing switch

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
| 1.1 | Manufacturer/Country of Origin |  | To be specified |  |
| 1.2 | Model type |  | To be specified |  |
| 1.3 | Applicable standard |  | IEC 62271-102 |  |
| 2 | Rated frequency, Hz |  | 50 |  |
| 3 | Method of neutral grounding |  | Directly earthed |  |
| 4 | Type |  | outdoor |  |
| 4.1 | Structure of one set |  | single phase/three phase |  |
| 4.2 | Break type |  | horizontal break |  |
| 4.2 | Number of earthing switches can be equipped for disconnector |  | (0, 1, 2) earthing blade |  |
| 5 | Voltage parameters |  |  |  |
| 5.1 | System voltage | kV | 110 |  |
| 5.2 | Maximum voltage | kV | 121 |  |
| 5.3 | Rated voltage | kV | ≥123 |  |
| 5.4 | Rated short-duration power-frequency withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV | ≥230 ≥265 |  |
| 5.5 | Rated lightning impulse withstand voltage (1,2/50 µs-BIL) + Phase-to-Earth + Across the isolating distance + Between phases | kV peak | ≥550 ≥630 |  |
| 6 | Current parameters |  |  |  |
| 6.1 | Rated normal current Ir | A | ≥ 1250 |  |
| 6.2 | Rated short-time withstand current | kA rms | ≥40 |  |
| 6.3 | Rated duration of short-circuit | s | ≥1 |  |
| 6.4 | Rated peak withstand current | kA peak | ≥100 |  |
| 7 | Main circuit contact resistance | µΩ | To be specified |  |
| 8 | Earthing switch parameters |  |  |  |
| 8.1 | Rated short-circuit making current | kA | ≥40 |  |
| 8.2 | Rated withstand voltage between insulated terminals and bases earthed | kV | ≥160 |  |
| 9 | Operational capabilities of disconnector, earthing switch |  |  |  |
| 9.1 | Drive mechanism |  | Single phase/ three phase |  |
| 9.2 | Mechanical endurance class |  |  |  |
| - | Disconnector |  | M1 |  |
| - | Earthing switch |  | M0 |  |
| 9.3 | Total mechanical operating, no maintenance |  |  |  |
| - | Disconnector | times | ≥2000 |  |
| - | Earthing switch | times | ≥1000 |  |
| 9.4 | Operated lever |  | yes |  |
| 9.5 | Mechanical interlock (Disconnector and Earthing switch) |  | yes |  |
| 10 | Total weight | kg | To be specified |  |
| 11 | Required clearance |  |  |  |
| 11.1 | Phase to phase | mm | ≥ 1100 |  |
| 11.2 | Phase to earth | mm | ≥ 1100 |  |
| 12 | Poles post of disconnector |  |  |  |
| 12.1 | Applicable standard |  | IEC 60273 or equivalent |  |
| 12.2 | Material |  | Brown ceramic porcelain |  |
| 12.3 | Minimum creepage distance | mm/ kV | ≥25 |  |
| 12.4 | Total creepage distance | mm | To be specified |  |
| 12.5 | Withstand the impact loads of disconnector - Three phase disconnector/Earthing switch + Straight load Fa1, Fa2, kN + Cross load Fb1, Fb2, kN - Single phase disconnector/Earthing switch + Straight load Fa1, Fa2, kN + Cross load Fb1, Fb2, kN - Vertical Force, Fc, kN | kN | 0.5: Ir≤1600A 0.6: Ir>1600A 0.17: Ir≤1600A 0.2:Ir>1600A 0.8: Ir≤1600A 1.0: Ir>1600A 0.2: Ir≤1600A 0.3: Ir>1600A 1.0 |  |
| 12.6 | Maximum impact load when the disconnector operates | kN | To be specified |  |
| 12.7 | Minimum distance in static condition: - Between phase and earth | mm | 1100 |  |
|  | - Between phases, mm | mm | 1100 |  |
| 13 | Material of main contact |  | Copper, Copper alloy or silver/nickel plated aluminum alloy |  |
| 14 | Operating mechanism |  |  |  |
| 14.1 | Disconnector |  | Manual and/or electrical motor |  |
| 14.2 | Earthing switch |  | Manual and/or electrical motor |  |
| 15 | Local control cabinet of disconnector, earthing switch: |  |  |  |
| 15.1 | Cabinet enclosure material |  | Aluminum alloy or stainless steel (Inox 304) or galvanized steel and the cabinet surface can be painted suitable to requirements |  |
| 15.2 | Minimum protection class |  | IP55 |  |
| 15.3 | Minimum thickness of cabinet enclosure | mm | ≥2 |  |
| 15.4 | Limit switch contact of disconnector |  | ≥(2NO+2NC) |  |
| 15.5 | Auxiliary switch contact of disconnector |  | ≥(8NO+8NC) |  |
| 15.6 | Auxiliary switch contact of earthing switch |  | ≥(6NO+6NC) |  |
| 15.7 | Rated DC current of the auxiliary contact | A | 10 |  |
| 15.8 | DC current withstands short-time of the auxiliary contact |  | 100 A/30 ms |  |
| 15.9 | Selection switch of Local/Remote |  | yes |  |
| 15.10 | "Open/Close" push buttons of disconnector, earthing switch |  | yes |  |
| 15.11 | Motor and MCBs with auxiliary contacts have separate power supply |  | yes |  |
| 15.12 | Overcurrent and overload protection for the motor |  | yes |  |
| 15.13 | Drying system with temperature sensor, led lighting, drying and lighting have separate power supply by MCBs with auxiliary contacts |  | yes |  |
| 15.14 | Electrical interlock circuit between disconnector and earthing switch |  | yes |  |
| 16 | Supply voltage: |  |  |  |
| 16.1 | Motor | VDC | 220 (+10%; -15%) |  |
| 16.2 | Trip and Close | VDC | 220 (+10%; -15%) |  |
| 16.3 | Heating and Lighting | VAC | 220 (+10%; -15%) |  |
| 17 | Material of support structures for disconnector |  | Galvanized steel |  |
| 18 | HV terminals: |  |  |  |
| 18.1 | Materials |  | Aluminum alloy /copper |  |
| 18.2 | Dimensions |  | suitable for conductor |  |
| 18.3 | Bolt |  | Stainless steel |  |
| 19 | Catalogues |  | To be supplied |  |
| 20 | Requirements for testing (according to Technical Specification) |  | Yes |  |
| 21 | The remaining parameters or different will comply with the provisions of 1676/QĐ-EVNNPT (EVNNPT) |  | Yes |  |

500kv current transformer

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Model type |  | To be specified |  |
|  | Applicable standard |  | IEC 61869 (2016-04) |  |
|  | Type |  | Outdoor, single phase, top core, oil paper immersed |  |
|  | Rated voltage | kV | ≥550 |  |
|  | Frequency | Hz | 50 |  |
|  | Lightning impulse withstand voltage (1.2/50μs) | kV | ≥1550 |  |
|  | Switching impulse withstand voltage | kV | ≥1175 |  |
|  | Power frequency withstand voltage (01 minute) |  |  |  |
|  | - Primary windings | kV | ≥ 680 |  |
|  | - Secondary windings | kV | 03 |  |
|  | Housing insulator: |  |  |  |
|  | - Applicable standard |  | To be specified |  |
|  | - Material |  | Brown porcelain |  |
|  | - Minimum creepage distance | mm/ kV | 25 |  |
|  | - Total creepage distance | mm | ≥ 13750 |  |
|  | - Average diameter of insulator | mm | To be specified |  |
|  | - Minimum clearance between phase to earth | mm | Comply with IEC 60071-1 |  |
|  | Rated primary current | A | ≥3150 |  |
|  | Extended current rating |  | 120% of Rated |  |
|  | Rated transformation ratio |  |  |  |
| 13.1 | Type 1 | A | 1000-2000-3000-4000/1/1/1/1/1/1 |  |
|  | Rated thermal withstand current (1 sec.) | kA | 50 |  |
|  | Rated dynamic withstand current | kA | 125 |  |
|  | Maximum partial discharge level at 1.1Un (highest system voltage) | pC | To be specified |  |
|  | Number of secondary windings: |  |  |  |
| - | Type 1 |  | 06 |  |
|  | Core characteristics: Rated burden; accuracy class |  |  |  |
| 18.1 | Type 1: |  |  |  |
|  | - Core No.1, 2 |  | 15VA – Cl. 0.5 |  |
|  | - Core No. 3, 4, 5, 6 |  | 30VA – Cl. 5P20 |  |
|  | - All burdens, accuracy classes at all ratios |  | Yes |  |
|  | Limits of current error and phase displacement |  |  |  |
|  | - For secondary windings with class 0.5 (at 25%÷100% Rated Burden) |  | Comply with Table 201 (IEC 61869-2) |  |
|  | - For secondary windings with class 5P20 (at 25%÷100% Rated Burden) |  | Comply with Table 205 (IEC 61869-2) |  |
|  | Multi-Ratio shall be changed on secondary winding |  | Yes |  |
|  | Secondary winding resistance | Ω | To be specified |  |
|  | Knee-point voltage |  | To be specified |  |
|  | Temperature rise | oC | 65 |  |
|  | Terminal: |  |  |  |
|  | - Materials |  | To be specified |  |
|  | - Dimensions |  | To be specified |  |
|  | - Holes - No. , size and spacing |  | At least 6 holes |  |
|  | Total weight | kg | To be specified |  |
|  | Calculated wind load moment about base | kN | To be specified |  |
|  | Operating time of CT: |  |  |  |
|  | - Total operating time until maintain | Year | ≥ 10 |  |
|  | - Total operating time until replacement | Year | ≥ 20 |  |
|  | Approved by STAMEQ all CTs |  | As scope of supply |  |
|  | Supporting structure |  | As scope of supply |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Materials |  | hot dip galvanized steel |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 2384/QĐ-EVNNPT |  | Yes |  |

220kV Current Transformer

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 60044-1, 2 IEC 61869-1, 2 |  |
|  | Type |  | Outdoor, single phase, oil paper immersed, Top core, reinforce safety design |  |
|  | Rated voltage | kV | ≥245 |  |
|  | Frequency | Hz | 50 |  |
|  | Impulse Voltage (1.2/50µs) withstand | kV | ≥1050 |  |
|  | Power Frequency Voltage withstand |  |  |  |
| - | Primary windings | kV | ≥460 |  |
| - | Secondary windings | kV | 3 |  |
|  | Housing insulator: |  |  |  |
| - | Applicable standard |  | To be specified |  |
| - | Material |  | Brown porcelain |  |
| - | Minimum nominal creepage distance | mm/kV | ≥25 |  |
| - | Total Minimum nominal specific creepage distance | mm | ≥6125 |  |
| - | Average diameter of insulator |  | To be specified |  |
|  | Rated Primary Current |  |  |  |
| - | Type 1 | A | 3000 |  |
| - | Type 2 | A | 2000 |  |
|  | Phase to Earth Clearance | mm | ≥ 2100 |  |
|  | Extended Current Rating |  | 120% of Rated |  |
|  | Rated Transformation Ratios |  |  |  |
| - | Type 1 | A | 1200-2000-3000/1/1/1/1/1 |  |
| - | Type 2 | A | 800-1200-2000/1/1/1/1/1 |  |
|  | Rated Thermal Withstand Current (1 sec.) | kA | 50 |  |
|  | Rated Dynamic Withstand Current | kA | 125 |  |
|  | Operating time of CT |  |  |  |
| - | Total operating time until maintain | Year | ≥ 8 |  |
| - | Total operating time until replacement | Year | ≥ 20 |  |
|  | Maximum Partial Discharge Level at 1.1 Un (highest system voltage) | pC | To be specified |  |
|  | Secondary Winding Resistance | Ω | To be specified |  |
|  | Terminals |  |  |  |
| - | Materials |  | To be specified |  |
| - | Dimensions |  | To be specified |  |
| - | Number of hole (minimum 6 holes) |  | To be specified |  |
|  | Total Weight | kg | To be specified |  |
|  | Calculated Wind Load Moment about Base | kN | To be specified |  |
|  | Core Characteristics: Rated Burden, Accuracy Class (Type 1 & 2) |  |  |  |
| + | Core No. 1, 2 |  | 10VA - Cl 0.5 |  |
| + | Core No. 3, 4, 5 |  | 30VA - Cl 5P20 |  |
|  | All burdens, accuracy Classes at all ratios |  | Yes |  |
|  | Limits of current error and phase displacement |  |  |  |
| - | For secondary windings with class 0.5 (at 25%÷100% Rated Burden) |  | Comply with: Table 11 - IEC 60044-1 or Table 201-IEC 61869-1 |  |
| - | For secondary windings with class 5P20 (at 25%÷100% Rated Burden) |  | Comply with: Table 14 - IEC 60044-1 or Table 205-IEC 61869-1 |  |
|  | Multi-Ratio shall be changed on secondary winding |  | Yes |  |
|  | Approved by STAMEQ |  | As Scope of Supply |  |
|  | Temperature rise | 0C | 65 |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 0063/QĐ-EVNNPT |  | Yes |  |

500kV Capacitor Voltage Transformer

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Catalogue number |  | To be specified |  |
|  | Applicable standard |  | IEC 61869-5 |  |
|  | Type |  | Outdoor, single phase, oil immersed |  |
|  | Rated voltage | kV | ≥550 |  |
|  | Frequency | Hz | 50 |  |
|  | Lightning impulse withstand voltage (1.2/50μs) | kV | ≥1550 |  |
|  | Switching impulse withstand voltage | kV | ≥1175 |  |
|  | Power frequency withstand voltage (01 minute) |  |  |  |
|  | - Primary winding | kV | ≥680 |  |
|  | - Secondary winding | kV | ≥3 |  |
|  | Guaranteed limits of rated capacitance | % | To be specified |  |
|  | Rated maximum HF current | A | To be specified |  |
|  | Temperature co-efficient of capacitance per 0C |  | To be specified |  |
|  | Maximum partial/discharge level .pC | kV | To be specified |  |
|  | Housing insulator: |  |  |  |
|  | - Applicable standard |  | To be specified |  |
|  | - Material |  | Brown porcelain |  |
|  | - Minimum creepage distance | mm/ kV | ≥25 |  |
|  | - Total creepage distance | mm | ≥13750 |  |
|  | - Average diameter of insulator | mm | To be specified |  |
|  | - Minimum clearance between phase to earth | mm | Comply with IEC 60071-1 |  |
|  | Rated mechanical terminal load | kN | 02 |  |
|  | Facilities for fitting of line trap |  | If any |  |
|  | Maximum permissible top wind loading | km/hr | To be specified |  |
|  | Calculated wind load moment about base | kN | To be specified |  |
|  | Flux density at rated voltage | Tesla | To be specified |  |
|  | Recommended fuse ratings |  |  |  |
|  | Weight of intermediate voltage transformer | kg | To be specified |  |
|  | Oil outlet and oil test valve | Yes | To be specified |  |
|  | Voltage ratio, burden, accuracy class |  |  |  |
|  | - Winding No.1 |  | 500kV:√3/110V:√3 25VA – Cl. 0.5 |  |
|  | - Winding No.2 |  | 500kV:√3/110V:√3 50VA – Cl. 3P |  |
|  | Over-voltage capability |  |  |  |
|  | - Continuous |  | 1.2 Ur |  |
|  | - 30 sec. |  | 1.5 Ur |  |
|  | Temperature rise | 0C | ≤65 |  |
|  | HV terminals: |  | To be specified |  |
|  | - Material |  |  |  |
|  | - Dimensions |  |  |  |
|  | - Holes - No. , size and spacing |  | At least 6 holes |  |
|  | Weight of capacitor voltage transformer | kg | To be specified |  |
|  | Approved by STAMEQ for all CVTs |  | As Sope of Supply |  |
|  | Operating time of CVT: |  |  |  |
|  | - Total operating time until maintain | Year | ≥ 10 |  |
|  | - Total operating time until replacement | Year | ≥ 20 |  |
|  | Supporting structure |  | As Scope of Supply |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Materials |  | hot dip galvanized steel |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 2386/QĐ-EVNNPT |  | Yes |  |

220kV Capacitor Voltage Transformer

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 60044-2, IEC 60044-5, IEC 61869-5, IEC 60815, IEC 60071, IEC 60137 (2008), IEC 60358-3 (2013) |  |
|  | Type |  | Outdoor, single phase, oil paper immersed, |  |
|  | Rated voltage | kV | ≥245 |  |
|  | Frequency | Hz | 50 |  |
|  | Impulse Voltage (1.2/50µs) Withstand | kV peak | ≥1050 |  |
|  | Power Frequency Voltage Withstand |  |  |  |
| - | Primary windings | kV rms. | ≥460 |  |
| - | Secondary windings | kV | ≥3 |  |
|  | Rated Maximum HF Current | A | To be specified |  |
|  | Temperature Co-efficient of capacitance per oC |  | To be specified |  |
|  | Maximum Partial/Discharge Level .pC | kV | To be specified |  |
|  | Housing insulator: |  |  |  |
| - | Applicable standard |  | To be specified |  |
| - | Material |  | Brown porcelain |  |
| - | Minimum nominal creepage distance | mm/kV | ≥25 |  |
| - | Minimum nominal specific creepage distance | mm | ≥6125 |  |
| - | Average diameter of insulator | mm | To be specified |  |
|  | Phase to Earth Clearance | mm | ≥ 2100 |  |
|  | Rated Mechanical Terminal Load | kN | To be specified |  |
|  | Facilities for fitting of line trap |  | If any |  |
|  | Max. Permissible Top Wind Loading | km/hr | To be specified |  |
|  | Calculated Wind Load Moment about Base | kNm | To be specified |  |
|  | HV Terminals |  | To be specified |  |
| - | Material |  |  |  |
| - | Dimensions |  |  |  |
| - | Number of hole (minimum 6 holes) or stud type |  | To be specified |  |
|  | Weight of capacitor voltage transformer | kg | To be specified |  |
|  | Flux Density at Rated Voltage | Tesla | To be specified |  |
|  | Recommended Fuse Ratings |  | To be specified |  |
|  | Weight of Intermediate Voltage Transformer | kg | To be specified |  |
|  | Oil outlet and oil test valve |  | Yes |  |
|  | Voltage ratio, burden, accuracy class |  |  |  |
| 25.1 | Ratio |  |  |  |
| - | Winding No.1 |  | 220kV:√3 /110V:√3 25VA - Cl 0.5 |  |
| - | Winding No.2 |  | 220kV:√3 /110V:√3 50VA - 3P |  |
|  | Maximum simultaneous burden output/ accuracy class |  | 25VA for class 0.5 50VA for class 3P |  |
|  | Limits of voltage error and phase displacement |  |  |  |
| - | For secondary windings with class 0.5 (at 25%÷100% Rated Burden) |  | Comply with: Table 11 - IEC 60044-2 or Table 501-IEC 61869-5 |  |
| - | For secondary windings with class 5P20 (at 25%÷100% Rated Burden) |  | Comply with: Table 12 - IEC 60044-2 or Table 502-IEC 61869-5 |  |
|  | Approved by STAMEQ for all CVTs |  | As Scope of Supply |  |
|  | Over volt capability |  |  |  |
| - | Continuous |  | 1.2x220kV/√3 |  |
| - | 30 sec |  | 1.5x220kV/√3 |  |
|  | Temperature rise | 0K | ≤65 |  |
|  | Requirements for testing according to Technical Specification) |  | Yes |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 0063/QĐ-EVNNPT |  | Yes |  |

220kV TRV Capacitor

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 60044-2, IEC 60044-5, IEC 61869-5, IEC 60815, IEC 60071, IEC 60137 (2008), IEC 60358-3 (2013) |  |
|  | Type |  | Outdoor, single phase, oil paper immersed, |  |
|  | Rated voltage | kV | ≥245 |  |
|  | Frequency | Hz | 50 |  |
|  | Impulse Voltage (1.2/50µs) Withstand | kV peak | ≥1050 |  |
|  | Power Frequency Voltage Withstand |  |  |  |
| - | Primary windings | kV rms. | ≥460 |  |
| - | Secondary windings | kV | ≥3 |  |
|  | Rated Maximum HF Current | A | To be specified |  |
|  | Temperature Co-efficient of capacitance per oC |  | To be specified |  |
|  | Maximum Partial/Discharge Level .pC | kV | To be specified |  |
|  | Housing insulator: |  |  |  |
| - | Applicable standard |  | To be specified |  |
| - | Material |  | Brown porcelain |  |
| - | Minimum nominal creepage distance | mm/kV | ≥25 |  |
| - | Minimum nominal specific creepage distance | mm | ≥ 6125 |  |
| - | Average diameter of insulator | mm | To be specified |  |
|  | Phase to Earth Clearance | mm | ≥ 2100 |  |
|  | Rated Mechanical Terminal Load | kN | To be specified |  |
|  | Facilities for fitting of line trap |  | If any |  |
|  | Max. Permissible Top Wind Loading | km/hr | To be specified |  |
|  | Calculated Wind Load Moment about Base | kNm | To be specified |  |
|  | HV Terminals |  | To be specified |  |
| - | Material |  |  |  |
| - | Dimensions |  |  |  |
| - | Number of hole (minimum 6 holes) or stud type |  | To be specified |  |
|  | Weight of capacitor voltage transformer | kg | To be specified |  |
|  | Flux Density at Rated Voltage | Tesla | To be specified |  |
|  | Recommended Fuse Ratings |  | To be specified |  |
|  | Weight of Intermediate Voltage Transformer | kg | To be specified |  |
|  | Oil outlet and oil test valve |  | Yes |  |
|  | Capacitance | nF | 15 |  |
|  | Limits of voltage error and phase displacement |  |  |  |
| - | For secondary windings with class 0.5 (at 25%÷100% Rated Burden) |  | Comply with: Table 11 - IEC 60044-2 or Table 501-IEC 61869-5 |  |
| - | For secondary windings with class 5P20 (at 25%÷100% Rated Burden) |  | Comply with: Table 12 - IEC 60044-2 or Table 502-IEC 61869-5 |  |
|  | Approved by STAMEQ for all CVTs |  | As Scope of Supply |  |
|  | Over volt capability |  |  |  |
| - | Continuous |  | 1.2x220kV/√3 |  |
| - | 30 sec |  | 1.5x220kV/√3 |  |
|  | Temperature rise | 0K | 65 |  |
|  | Requirements for testing according to Technical Specification) |  | Yes |  |
|  | Catalogues |  | To be supplied |  |

Notes:

All 220kV, 110kV CVT from ABB - INDIA shall not be eligible (EVNNPT has declared that all equipment 220kV, 110kV CVT (WP 245 N2 and WN 145 N2) from ABB-India shall not be allowed for bid according to EVNNPT official document No. 1762/EVNNPT-KT, dated 19/05/2021;

110kV TRV Capacitor

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 60044-2, IEC 60044-5, IEC 61869-5, IEC 60815, IEC 60071, IEC 60137 (2008), IEC 60358-3 (2013) |  |
|  | Type |  | Outdoor, single phase, oil paper immersed, |  |
|  | Rated voltage | kV | ≥123 |  |
|  | Frequency | Hz | 50 |  |
|  | Impulse Voltage (1.2/50µs) Withstand | kV peak | ≥550 |  |
|  | Power Frequency Voltage Withstand |  |  |  |
| - | Primary windings | kV rms. | ≥230 |  |
| - | Secondary windings | kV | ≥3 |  |
|  | Rated Maximum HF Current | A | To be specified |  |
|  | Temperature Co-efficient of capacitance per oC |  | To be specified |  |
|  | Maximum Partial/Discharge Level .pC | kV | To be specified |  |
|  | Housing insulator: |  |  |  |
| - | Applicable standard |  | To be specified |  |
| - | Material |  | Brown porcelain |  |
| - | Minimum nominal creepage distance | mm/kV | ≥25 |  |
| - | Minimum nominal specific creepage distance | mm | ≥ 3075 |  |
| - | Average diameter of insulator | mm | To be specified |  |
|  | Phase to Earth Clearance | mm | ≥ 1100 |  |
|  | Rated Mechanical Terminal Load | kN | To be specified |  |
|  | Facilities for fitting of line trap |  | If any |  |
|  | Max. Permissible Top Wind Loading | km/hr | To be specified |  |
|  | Calculated Wind Load Moment about Base | kNm | To be specified |  |
|  | HV Terminals |  | To be specified |  |
| - | Material |  |  |  |
| - | Dimensions |  |  |  |
| - | Number of hole (minimum 6 holes) or stud type |  | To be specified |  |
|  | Weight of capacitor voltage transformer | kg | To be specified |  |
|  | Flux Density at Rated Voltage | Tesla | To be specified |  |
|  | Recommended Fuse Ratings |  | To be specified |  |
|  | Weight of Intermediate Voltage Transformer | kg | To be specified |  |
|  | Oil outlet and oil test valve |  | Yes |  |
|  | Capacitance | nF | 10 |  |
|  | Limits of voltage error and phase displacement |  |  |  |
| - | For secondary windings with class 0.5 (at 25%÷100% Rated Burden) |  | Comply with: Table 11 - IEC 60044-2 or Table 501-IEC 61869-5 |  |
| - | For secondary windings with class 5P20 (at 25%÷100% Rated Burden) |  | Comply with: Table 12 - IEC 60044-2 or Table 502-IEC 61869-5 |  |
|  | Approved by STAMEQ for all CVTs |  | As Scope of Supply |  |
|  | Over volt capability |  |  |  |
| - | Continuous |  | 1.2x110kV/√3 |  |
| - | 30 sec |  | 1.5x110kV/√3 |  |
|  | Temperature rise | 0K | 65 |  |
|  | Requirements for testing according to Technical Specification) |  | Yes |  |
|  | Catalogues |  | To be supplied |  |

Notes:

All 220kV, 110kV CVT from ABB - INDIA shall not be eligible (EVNNPT has declared that all equipment 220kV, 110kV CVT (WP 245 N2 and WN 145 N2) from ABB-India shall not be allowed for bid according to EVNNPT official document No. 1762/EVNNPT-KT, dated 19/05/2021;

220kV Current limiting reactor

| No. | Description | Unit | Requirement | Offered |
| --- | --- | --- | --- | --- |
| 1 | Manufacture/Country of Origin |  | To be specified |  |
| 2 | Ordering number |  | To be specified |  |
| I | Substantial requirements |  |  |  |
| 1 | Applicable standard |  | IEC 60076-6 2007 and/or IEEE C57.16-2011 |  |
| 2 | Type |  | Outdoor, Air-core dry type, single phase |  |
| 3 | Equipment highest voltage | kV | ≥245 |  |
| 4 | Rated frequency | Hz | 50 |  |
| 5 | Number of phases |  | Bank of Single phases (one coil per phase) |  |
| 6 | Rated continuous current | A | ≥3150 |  |
| 7 | Mechanical short circuit current withstands | kA | ≥50 |  |
| 8 | Thermal short circuit current withstands | kA/2s | ≥15 |  |
| 10 | Output number of terminal connectors for CLR |  | 3 |  |
| 11 | Insulation level IEC 76-3 |  |  |  |
|  | Basic Impulse Level | kVp | ≥1050 |  |
|  | Power frequency withstand voltage | kV.rms | ≥460 |  |
| 12 | Impedance per phase | Ω | 7.5Ω (24mH) |  |
| 13 | Type of cooling |  | Natural air |  |
| 14 | Total losses per phase /at nominal capacity: | kW | To be specified |  |
| 15 | Total mass (include insulators, pedestals…) | kg | To be specified |  |
| 16 | Transportation mass (coil only) | kg | To be specified |  |
| 17 | Thermal class |  | At least, F |  |
| 18 | Dimensions (mm) |  | Dimensions of CLRs shall fit with layout in attached drawings of Bidding documents |  |
| - | Outer Diameter (with Corona rings) | mm | To be specified |  |
| - | Minimum distances between the centers of coils (mm): | mm | To be specified |  |
| - | Outer Diameter of Top Hat | mm | To be specified |  |
| - | Height (include insulators, pedestals … | mm | To be specified |  |
| - | Height of insulators, pedestals | mm | To be specified |  |
| 19 | Mounting arrangement |  | Side-by-side |  |
| 20 | No-load loss, kW |  | To be specified |  |
| 21 | Guaranteed value of sound level for unit | dB(A) | ≤ 75 dBA (2m from coil surface) |  |
| 22 | Winding insulation design |  | Uniform |  |
| 23 | In-Service Duty |  | 100% |  |
| 24 | Design |  | Cylindrical coil encapsulated with fiberglass impregnated epoxy resin |  |
|  |  |  | Conductor material: Aluminum Coil axis: vertical Side by side mounting |  |
|  |  |  | Heavy pollution considered, minimum insulator creepage: > 25 mm/kV |  |
|  |  |  | Seismic considered: 0.2g horizontal ground acceleration |  |
|  |  |  | Coil painted ASA 70 or RAL 7035 (light grey) |  |
| II | BASE INSULATOR |  |  |  |
| 1 | Type |  | Station post insulator, outdoor |  |
| 2 | Manufacturer/Country of origin |  | To be specified |  |
| 3 | Applied Standard |  | IEC 273 and/or IEC 60168 |  |
| 4 | Material |  | Porcelain |  |
| 5 | Insulator color |  | ANSI-70 light gray or equivalent |  |
| 6 | Minimum nominal creepage distance |  | ≥ 25mm/kV |  |
| 7 | Insulation level IEC 273 |  |  |  |
|  | - Basic Impulse Level |  | 1050 kVp |  |
|  | - Power frequency withstand voltage |  | 460 kV r.m.s |  |
| 8 | Minimum failing load: |  |  |  |
|  | - Bending |  | To be specified |  |
|  | - Torsion |  | To be specified |  |
| III | SUPPORT STRUCTURE |  |  |  |
| 1 | Support structure, included anchor bolts, plates… |  | Provided with reactors |  |

110kV Current limiting reactor

| No. | Description | Unit | Requirement | Offered |
| --- | --- | --- | --- | --- |
| 1 | Manufacture/Country of Origin |  | To be specified |  |
| 2 | Ordering number |  | To be specified |  |
| I | Substantial requirements |  |  |  |
| 1 | Applicable standard |  | IEC 60076-6 2007 and/or IEEE C57.16-2011 |  |
| 2 | Type |  | Outdoor, Air-core dry type, single phase |  |
| 3 | Equipment highest voltage | kV | ≥123 |  |
| 4 | Rated frequency | Hz | 50 |  |
| 5 | Number of phases |  | Bank of Single phases (one coil per phase) |  |
| 6 | Rated continuous current | A | ≥2000 |  |
| 7 | Mechanical short circuit current withstands | kA | ≥40 |  |
| 8 | Thermal short circuit current withstands | kA/2s | ≥15 |  |
| 10 | Output number of terminal connectors for CLR |  | 3 |  |
| 11 | Insulation level IEC 76-3 |  |  |  |
|  | Basic Impulse Level | kVp | ≥550 |  |
|  | Power frequency withstand voltage | kV.rms | ≥230 |  |
| 12 | Impedance per phase | Ω | 7.5Ω (24mH) |  |
| 13 | Type of cooling |  | Natural air |  |
| 14 | Total losses per phase /at nominal capacity: | kW | To be specified |  |
| 15 | Total mass (include insulators, pedestals…) | kg | To be specified |  |
| 16 | Transportation mass (coil only) | kg | To be specified |  |
| 17 | Thermal class |  | At least, F |  |
| 18 | Dimensions (mm) |  | Dimensions of CLRs shall fit with layout in attached drawings of Bidding documents |  |
| - | Outer Diameter (with Corona rings) | mm | To be specified |  |
| - | Minimum distances between the centers of coils (mm): | mm | To be specified |  |
| - | Outer Diameter of Top Hat | mm | To be specified |  |
| - | Height (include insulators, pedestals … | mm | To be specified |  |
| - | Height of insulators, pedestals | mm | To be specified |  |
| 19 | Mounting arrangement |  | Side-by-side |  |
| 20 | No-load loss, kW |  | To be specified |  |
| 21 | Guaranteed value of sound level for unit | dB(A) | ≤ 75 dBA (2m from coil surface) |  |
| 22 | Winding insulation design |  | Uniform |  |
| 23 | In-Service Duty |  | 100% |  |
| 24 | Design |  | Cylindrical coil encapsulated with fiberglass impregnated epoxy resin |  |
|  |  |  | Conductor material: Aluminum Coil axis: vertical Side by side mounting |  |
|  |  |  | Heavy pollution considered, minimum insulator creepage: > 25 mm/kV |  |
|  |  |  | Seismic considered: 0.2g horizontal ground acceleration |  |
|  |  |  | Coil painted ASA 70 or RAL 7035 (light grey) |  |
| II | BASE INSULATOR |  |  |  |
| 1 | Type |  | Station post insulator, outdoor |  |
| 2 | Manufacturer/Country of origin |  | To be specified |  |
| 3 | Applied Standard |  | IEC 273 and/or IEC 60168 |  |
| 4 | Material |  | Porcelain |  |
| 5 | Insulator color |  | ANSI-70 light gray or equivalent |  |
| 6 | Minimum nominal creepage distance |  | ≥ 25mm/kV |  |
| 7 | Insulation level IEC 273 |  |  |  |
|  | - Basic Impulse Level |  | 550 kVp |  |
|  | - Power frequency withstand voltage |  | 230 kV r.m.s |  |
| 8 | Minimum failing load: |  |  |  |
|  | - Bending |  | To be specified |  |
|  | - Torsion |  | To be specified |  |
| III | SUPPORT STRUCTURE |  |  |  |
| 1 | Support structure, included anchor bolts, plates… |  | Provided with reactors |  |

35kV Inductive Voltage Transformer

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Model type |  | To be specified |  |
|  | Applicable standard |  | IEC 61869-3/ IEC 60044-2/ IEC 61869-1 |  |
|  | Type |  | Outdoor, single phase, oil immersed or solid insulation (Epoxy Resin) |  |
|  | Rated voltage | kV | ≥38.5 |  |
|  | Frequency | Hz | 50 |  |
|  | Lightning impulse withstand voltage (1.2/50μs) | kV peak | ≥180 |  |
|  | Power frequency withstand voltage (01 minute) |  |  |  |
|  | - Primary winding | kV | ≥75 |  |
|  | - Secondary winding | kV | ≥3 |  |
|  | Housing insulator: |  |  |  |
|  | - Applicable standard |  | To be specified |  |
|  | - Material |  | Brown porcelain |  |
|  | - Minimum creepage distance | mm/ kV | ≥25 |  |
|  | - Total creepage distance | mm | ≥600 |  |
|  | - Average diameter of insulator | mm | To be specified |  |
|  | - Minimum clearance between phase to earth | mm | Comply with IEC 60071-1 |  |
|  | Rated mechanical terminal load | kN | 02 |  |
|  | Maximum permissible top wind loading | km/hr | To be specified |  |
|  | Calculated wind load moment about base | kN | To be specified |  |
|  | Flux density at rated voltage | Tesla | To be specified |  |
|  | Recommended fuse ratings |  | To be specified |  |
|  | Oil outlet and oil test valve | Yes | To be specified |  |
|  | Voltage ratio, burden, accuracy class |  |  |  |
|  | - Winding No.1 |  | 35kV:√3/110V:√3 15VA – Cl. 0.5 |  |
|  | - Winding No.2 |  | 35kV:√3/110V: √3 25VA – Cl. 3P |  |
|  | - Winding No.3 |  | 35kV:√3/110V: 3 25VA – Cl. 6P |  |
|  | Partial discharge level: limit shall not be exceeded at the partial discharge test voltage 1.2xUm/√3 |  |  |  |
|  | - Solid insulation | pC | 20 |  |
|  | - Immersion in liquid | pC | 05 |  |
|  | Over-voltage capability |  |  |  |
|  | - Continuous |  | 1.2x35kV/√3 |  |
|  | - 8 hours |  | 1.9x35kV/√3 |  |
|  | Temperature rise | C | ≤60 |  |
|  | HV terminals: |  | To be specified |  |
|  | - Material |  |  |  |
|  | - Dimensions |  |  |  |
|  | - Holes - No. , size and spacing |  | At least 6 holes |  |
|  | Weight of inductive voltage transformer | kg | To be specified |  |
|  | Approved by STAMEQ for all CVTs |  | As scope of supply |  |
|  | Second terminal box cover design, lead hole |  | - The secondary terminal cover is made of aluminum, aluminum alloy, stainless steel or hot-dip galvanized sheet steel. - The lid of the box or the base of the box and the bolts of the lid must have holes drilled to thread the sealing lead. |  |
|  | Connector label |  | The connector label shall allow identification of: - Primary and secondary coils. - Parts of the coil (if any). - The relevant poles of the coil and the coil. - Intermediate steps (if any). Terminals shall be clearly and conspicuously marked on the surface or vicinity of the connector. This labeling must include: - The letters are placed after or before the numbers. The letters must be capital letters. - Symbols of voltage transformer terminals shall be in accordance with relevant TCVN or IEC standards |  |
|  | Operating time of VT: |  |  |  |
|  | - Total operating time until maintain | Year | To be specified |  |
|  | - Total operating time until replacement | Year | To be specified |  |
|  | Supporting structure |  | As scope of supply |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Materials |  | hot dip galvanized steel |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 104/QĐ-HĐTV of EVN |  | Yes |  |

500kv surge arrester

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Model type |  | To be specified |  |
|  | Applicable standard |  | IEC 60099-4 |  |
|  | Type |  | Outdoor, ZnO, gapless |  |
|  | Rated voltage | kV | ≥420 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Maximum continuous operating voltage (Uc) | kV | 336 |  |
|  | Temporary overvoltage for 1 sec. | kV | To be specified |  |
|  | Rated insulation level |  |  |  |
|  | - Lightning impulse withstand voltage | kVp | ≥1550 |  |
|  | - Switching impulse withstand voltage | kVp | ≥1175 |  |
|  | - Power frequency withstand voltage( 1 minutes) | kV | ≥680 |  |
|  | Power frequency reference voltage | kV | To be specified |  |
|  | - at reference current of | mA | To be specified |  |
|  | Note: State peak value or rms. |  |  |  |
|  | Nominal discharge current | kA | 20 |  |
| - N | Rated short cicuit curent | kA | ≥50 |  |
|  | Maximum withstand current 4/10µs | kAp | 100 |  |
|  | IEC long duration discharge class |  | 5 |  |
|  | Pressure relief class and corresponding fault current | kA | To be specified |  |
|  | energy absorption capability | kJ/kV Ur | ≥10 |  |
|  | Maximum residual voltage of complete arrester for |  |  |  |
|  | (a) Nominal discharge current impulse with rise time 1µs | kV | To be specified |  |
|  | (b) Nominal discharge current 8/20µs-20kA impulse |  |  |  |
|  | Steep impulse | kV peak | ≤ 2.8 x Ur |  |
|  | Lightning impulse | kV peak | ≤ 2.5 x Ur |  |
|  | Switching impulse | kV peak | ≤ 2.1 x Ur |  |
|  | (c) Switching impulse | kV | To be specified |  |
|  | Wave shape | µs | To be specified |  |
|  | With peak current of | A | To be specified |  |
|  | Standard to which arrester is tested |  | IEC 60099-4 |  |
|  | Leakage current through the complete arrester at max. continuous operating voltage |  | To be specified |  |
|  | - resistive component | mA |  |  |
|  | - capacitive component | mA |  |  |
|  | (state whether peak or rms. value) |  |  |  |
|  | Material employed in series non-linear resistor |  | ZnO |  |
|  | Sensitivity of surge counter: |  | To be specified |  |
|  | (a) Current | A |  |  |
|  | (b) Corresponding wave shape | µs |  |  |
|  | Peak voltage across surge counter when a 8/20µs current surge of peak value equal to the nominal discharge current of the arrester is applied | V | To be specified |  |
|  | RMS voltage across surge counter when continuous operating voltage is applied to arrester | V | To be specified |  |
|  | Leakage current meter range |  |  |  |
|  | Arrester housing: |  |  |  |
|  | - Material |  | Porcelain or polymer (Silicone rubber) |  |
|  | - Lightning impulse withstand | kV | To be specified |  |
|  | - Switching impulse withstand | kV | To be specified |  |
|  | - Power frequency withstand | kV (rms.) | To be specified |  |
|  | - Minimum nominal creepage distance | mm/kV | ≥25 |  |
|  | - Minimum nominal specific creepage distance | mm | ≥ 13750 |  |
|  | Average diameter of insulator | mm | To be specified |  |
|  | Phase to Earth Clearance | mm | Comply with IEC 60071-1 |  |
|  | Voltage grading ring | mm | Yes |  |
|  | Diameter of voltage grading ring | mm | To be specified |  |
|  | Seismic withstand capability |  | To be specified |  |
|  | Calculated Wind Load Moment about the base of the arrester | kN-m | To be specified |  |
|  | Cantilever strength of arrester | kN-m | To be specified |  |
|  | Terminal materials/dimension |  | To be specified |  |
|  | - Holes - No. , size and spacing |  | At least 6 holes |  |
|  | Surge counter |  | To be specified |  |
|  | - Minimum count current | A | To be specified |  |
|  | - Maximum high current withstand (4/10s) | kA | To be specified |  |
|  | - Maximum residual voltage at 100kA (4/10s) | kVpeak | To be specified |  |
|  | - Surge counting time resolution | s | To be specified |  |
|  | Scale range of ammeter | A | To be specified |  |
|  | Indication of counter |  | To be specified |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes |  |
|  | Supporting structure |  | As scope of supply |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Materials |  | hot dip galvanized steel |  |
|  | Catalogues |  | To be supplied |  |
|  | Total operating time duration under rated conditions | Year | To be specified |  |
|  | Number of surge arrester operator at nominal discharge current | times | To be specified |  |
|  | Current leakage meter is capable of transmitting signal to the control room of the substation equipped with surge arrester for online monitoring of current leakage |  | Yes |  |
|  | The remaining parameters or different will comply with the provisions of 123/QĐ-HĐTV of EVNNPT |  | Yes |  |

220kV SURGE ARRESTER

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 60099-4, -5 |  |
|  | Type |  | Outdoor, ZnO, gapless |  |
|  | Rated voltage (Ur) | kV | 192 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Maximum continuous operating voltage (UC) | kV | ≥ 154 |  |
|  | Temporary overvoltage for 1 sec. | kV | To be specified |  |
|  | Rated insulation level |  |  |  |
| - | Lightning impulse withstand voltage | kVrms | ≥1050 |  |
| - | Power frequency withstand voltage | kVp | ≥460 |  |
|  | Nominal discharge current | kA | ≥10 |  |
|  | Rated short-time withstand current (Is) | kA | ≥ 50 |  |
|  | IEC long duration discharge class |  | 3 |  |
|  | Minimum energy absorption capability | kJ/kV (Ur) | 7 |  |
|  | Residual voltage with 10kA discharge current |  |  |  |
| - | Slope impulse | kV | ≤ 2.8 x Ur |  |
| - | Lightning impulse | kV | ≤ 2.5 x Ur |  |
| - | Switching impulse | kV | ≤ 2.1 x Ur |  |
|  | High current impulse (4/10µs) withstand | kA peak | 100 |  |
|  | Standard to which arrester is tested |  | IEC 60099-4 |  |
|  | Leakage current through the complete arrester at max. continuous operating voltage |  | To be specified |  |
| - | Resistive component | mA |  |  |
| - | Capacitive component | mA |  |  |
|  | (state whether peak or rms. value) |  |  |  |
|  | Material employed in series non-linear resistor |  | ZnO |  |
|  | Sensitivity of surge counter: |  | To be specified |  |
|  | (a) Current | A |  |  |
|  | (b) Corresponding wave shape | µs |  |  |
|  | Peak voltage across surge counter when a 8/20µs current surge of peak value equal to the nominal discharge current of the arrester is applied | V | To be specified |  |
|  | RMS voltage across surge counter when continuous operating voltage is applied to arrester | V | To be specified |  |
|  | Surge counter displays digitally when surge arrester discharges (local display or signal transmission to remote monitoring equipment). |  | Yes |  |
|  | The current leakage meter continuously monitors the leakage current of the surge arrester in real time. The indicator mechanism of the meter can be used: a hand indicator type or a numerical display type. If the hand indicator: on the dial there is a limit value (if displayed as a number with a warning light) of the current leakage: good level, the alarm level should be separated from operation. These value limits are displayed locally or transmitted to a remote monitoring device. |  | Yes |  |
|  | The leakage current meter has the ability to transmit signals to the substation control room for online monitoring of leakage current |  | Yes |  |
|  | Leakage current meter range |  | To be specified |  |
|  | Arrester housing: |  |  |  |
| - | Material |  | Porcelain or Polymer |  |
| - | Lightning impulse withstand | kV | To be specified |  |
| - | Switching impulse withstand | kV | To be specified |  |
| - | Power frequency withstand | kArms. | To be specified |  |
| - | Minimum nominal creepage distance | mm/kV | ≥25 |  |
| - | Minimum nominal specific creepage distance | mm | ≥6125 |  |
| - | Average diameter of insulator | mm | To be specified |  |
|  | Phase to Earth Clearance | mm | ≥ 2100 |  |
|  | Voltage grading ring | mm | To be specified |  |
|  | Diameter of voltage grading ring (if fitted) | mm | To be specified |  |
|  | Seismic withstand capability |  | To be specified |  |
|  | Calculated Wind Load Moment about the base of the arrester | kN-m | To be specified |  |
|  | Cantilever strength of arrester | kN-m | To be specified |  |
|  | Terminal materials/dimension |  | To be specified |  |
|  | Material |  |  |  |
|  | Dimensions |  |  |  |
|  | Number of hole (minimum 6 holes) |  |  |  |
|  | Surge counter |  | Yes |  |
| - | Minimum count current | A | To be specified |  |
| - | Maximum high current withstand (4/10s) | kA | To be specified |  |
| - | Maximum residual voltage at 100kA (4/10s) | kVpeak | To be specified |  |
| - | Surge counting time resolution | s | To be specified |  |
| - | Scale range of ammeter | A | To be specified |  |
| - | Indication of counter |  | To be specified |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes |  |
|  | Catalogues |  | To be supplied |  |
|  | Total operating time duration under rated conditions | Year | To be supplied |  |
|  | Number of surge arrester operator at nominal discharge current | times | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 0170/QĐ-HĐTV |  | Yes |  |

500kV Post Insulator

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Model type |  | To be specified |  |
|  | Applicable standard |  | IEC 60273 |  |
|  | Insulator material |  | Porcelain |  |
|  | Type |  | C10-1550 |  |
|  | Dimensions (State Tolerances.): |  |  |  |
|  | - Height | mm | To be specified |  |
|  | - Average diameter of insulator | mm | To be specified |  |
|  | Minimum nominal creepage distance | mm/kV | ≥ 25 |  |
|  | Minimum nominal specific creepage distance | mm | ≥ 13750 |  |
|  | Phase to Earth Clearance | mm | Comply with IEC 60071-1 |  |
|  | Mechanical |  |  |  |
|  | - Minimum Failing Load-bending | kN | 10 |  |
|  | - Minimum Failing Moment-torsion | kNm | 4 |  |
|  | Electrical |  |  |  |
|  | Power Frequency Withstand Voltage |  |  |  |
|  | - Dry Withstand Voltage (1 min. 50Hz) | kV | 860 |  |
|  | - Wet Withstand Voltage (1 min. 50Hz) | kV | 680 |  |
|  | Light Impulse Voltage (1.2/50µs) Withstand |  |  |  |
|  | - Positive | kV peak | 1550 |  |
|  | - Negative | kV peak | 1550 |  |
|  | 50% Impulse Flashover Voltage |  | To be specified |  |
|  | - Positive | kV |  |  |
|  | - Negative | kV |  |  |
|  | Flashover Voltage |  | To be specified |  |
|  | - Dry Flashover Voltage (50 Hz) | kV |  |  |
|  | - Wet Flashover Voltage (50 Hz) | kV |  |  |
|  | Fixing Arrangements |  | To be specified |  |
|  | - Top Cap PCD | mm |  |  |
|  | - Top Cap Fixing Holes - number x size | mm | At least 6 holes |  |
|  | - Base PCD |  |  |  |
|  | - Base Fixing Holes - number x size |  | At least 6 holes |  |
|  | Weight of complete Post Insulator | kg | To be specified |  |
|  | Supporting structure |  | As scope of supply |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Materials |  | hot dip galvanized steel |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 0103/QĐ-EVNNPT |  | Yes |  |

220kV Post Insulator

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 60273 |  |
|  | Rated voltage | kV | ≥245 |  |
|  | Insulator material |  | Porcelain |  |
|  | Type |  | To be specified |  |
|  | Dimensions (State Tolerances.): |  |  |  |
| - | Height | mm | To be specified |  |
| - | Average diameter of insulator | mm | To be specified |  |
|  | Minimum nominal creepage distance | mm/kV | ≥25 |  |
|  | Total Minimum nominal specific creepage distance | mm | ≥ 6125 |  |
|  | Phase to Earth Clearance | mm | ≥ 2100 |  |
|  | Minimum insulation puncture voltage | kV | ≥ 1150 |  |
|  | Mechanical |  |  |  |
| - | Minimum Failing Load-bending | kN | 10 |  |
| - | Minimum Failing Moment-torsion | kNm | 4 |  |
|  | Electrical |  |  |  |
|  | a. Power Frequency Withstand Voltage |  |  |  |
| - | Dry Withstand Voltage (1 min. 50Hz) | kV | 550 |  |
| - | Wet Withstand Voltage (1 min. 50Hz) | kV | 460 |  |
|  | b. Light Impulse Voltage (1.2/50µs) Withstand |  |  |  |
| - | Positive | kV peak | 1050 |  |
| - | Negative | kV peak | 1050 |  |
|  | c. 50% Impulse Flashover Voltage |  | To be specified |  |
| - | Positive | kV |  |  |
| - | Negative | kV |  |  |
|  | d. Flashover Voltage |  | To be specified |  |
| - | Dry Flashover Voltage (50 Hz) | kV |  |  |
| - | Wet Flashover Voltage (50 Hz) | kV |  |  |
|  | Fixing Arrangements |  | To be specified |  |
| - | Top Cap PCD | mm |  |  |
| - | Top Cap Fixing Holes - number x size | mm |  |  |
| - | Base PCD |  |  |  |
| - | Base Fixing Holes - number x size |  |  |  |
|  | Weight of complete Post Insulator | kg | To be specified |  |
|  | Supporting clamp for |  | To be supplied |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 0103/QĐ-EVNNPT |  | Yes |  |

110KV POST INSULATOR

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacture/ Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 60273 |  |
|  | Rated voltage | kV | 123 |  |
|  | Insulator material |  | Porcelain |  |
|  | Type |  | To be specified |  |
|  | Dimensions (State Tolerances.): |  |  |  |
| - - | Height | mm | To be specified |  |
| - - | Average diameter of insulator | mm | To be specified |  |
|  | Minimum nominal creepage distance | mm/kV | 25 |  |
|  | Minimum nominal specific creepage distance | mm | To be specified |  |
|  | Phase to Earth Clearance | mm | ≥ 1100 |  |
|  | Mechanical |  |  |  |
| - - | + Minimum Failing Load-bending | kN | 10 |  |
| - | + Minimum Failing Moment-torsion | kNm | 4 |  |
|  | Electrical |  |  |  |
|  | a. Power Frequency Withstand Voltage | kV | 230 |  |
|  | b. Light Impulse Voltage (1.2/50µs) Withstand | kV peak | 550 |  |
|  | c. 50% Impulse Flashover Voltage |  | To be specified |  |
| - | Positive | kV |  |  |
| - | Negative | kV |  |  |
|  | d. Flashover Voltage |  | To be specified |  |
| - | Dry Flashover Voltage (50 Hz) | kV |  |  |
| - | Wet Flashover Voltage (50 Hz) | kV |  |  |
|  | Fixing Arrangements |  | To be specified |  |
| - | Top Cap PCD | mm |  |  |
| - - | Top Cap Fixing Holes - number x size | mm |  |  |
| - | - Base PCD |  |  |  |
| - | - Base Fixing Holes - number x size |  |  |  |
|  | - Weight of complete Post Insulator | kg | To be specified |  |
|  | - Type test and routine test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
|  | Catalogues |  | To be supplied |  |
|  | Supporting structure |  | As scope of supply |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Materials |  | hot dip galvanized steel |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes |  |
|  | Catalogues |  | To be supplied |  |

500kV SUSPENSION AND TENSION INSULATOR

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Insulator unit |  |  |  |
|  | Manufacturer/Country of Origin of insulator and Fitting of insulator string |  | To be specified |  |
|  | Catalogue number |  | To be specified |  |
|  | Model type |  |  |  |
| - | Tension insulator |  | U160BSP |  |
| - | Suspension insulator |  | U160BSP |  |
|  | Insulating material |  | Toughened glass |  |
|  | Applicable standard |  | IEC 60305 |  |
|  | Type of coupling |  | Ball & socket |  |
|  | Size of coupling | mm | To be specified |  |
|  | Locking device |  | Split pin type |  |
|  | Minimum electro-mechanical failing load |  |  |  |
|  | - Tension insulator | kN | 2x160 |  |
|  | - Suspension insulator | kN | 2x160 |  |
|  | Shed diameter | mm | To be specified |  |
|  | Unit spacing |  |  |  |
|  | - Tension insulator | mm | To be specified |  |
|  | - Suspension insulator | mm | To be specified |  |
|  | Minimum creepage distance | Mm | ≥ 440 |  |
|  | Total creepage distance | mm | ≥ 13750 |  |
|  | Wet power frequency withstand voltage - min. |  |  |  |
|  | - Tension insulator | kV | 55 |  |
|  | - Suspension insulator | kV | 55 |  |
|  | Dry power frequency withstand voltage-min. |  |  |  |
|  | - Tension insulator | kV | 90 |  |
|  | - Suspension insulator | kV | 90 |  |
|  | Lightning impulse withstand |  |  |  |
|  | - Tension insulator | kV | 140 |  |
|  | - Suspension insulator | kV | 140 |  |
|  | Minimum puncture voltage in oil | kV | 130 |  |
|  | Zinc sleeve |  | Yes |  |
|  | Insulator set complete |  |  |  |
|  | Number of insulator strings in parallel per phase |  |  |  |
|  | Minimum eletcro-mechanical failing load complete set |  |  |  |
|  | Tension insulator | kN | 2x160 |  |
|  | Suspension insulator | kN | 2x160 |  |
|  | Number of insulator disks in each string | disk | 2 x 34 |  |
|  | Overall length of set including clamp and all fittings |  | To be specified |  |
|  | - max | mm |  |  |
|  | - min | mm |  |  |
|  | Weight of complete set with all fittings | kg | To be specified |  |
|  | Turnbuckle for 500kV tension insulator |  | Yes |  |
|  | Arcing horn for 500kV insulator |  | Yes |  |
|  | Fittings |  |  |  |
|  | - Type of fittings |  | U bolted, M18 Horizontal approach |  |
|  | - Dimension of U bolted | mm | 90 |  |
|  | 50Hz flashover and withstand tests (complete sets) |  | To be specified |  |
|  | Dry flash over | kV |  |  |
|  | One minute wet withstand | kV |  |  |
|  | 50 percent impulse flashover |  | To be specified |  |
|  | 1.2/50µs negative wave | kV |  |  |
|  | 1.2/50µs positive wave | kV |  |  |
|  | Corona test voltage | kV | To be specified |  |
|  | Radio influence voltage measured at 1.1 times Us/√3 at 1MHz | µV | To be specified |  |

220kV Suspension and Tension Insulator

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Insulator unit |  |  |  |
| 1 | Manufacturer/Country of Origin of insulator and Fitting of insulator string |  | To be specified |  |
| 2 | Model type |  |  |  |
|  | Tension insulator |  | U120BP |  |
|  | Suspension insulator |  | U70BLP |  |
| 3 | Insulating material |  | Glass or ceramic |  |
| 4 | Applicable standard |  | IEC 60305 |  |
| 5 | Type of coupling |  | Ball & socket |  |
| 6 | Size of coupling | mm | To be specified |  |
| 7 | Locking device |  | Split pin type |  |
| 8 | Minimum electro-mechanical failing load |  |  |  |
|  | - Tension insulator | kN | ≥ 120 |  |
|  | - Suspension insulator | kN | ≥ 70 |  |
| 9 | Shed diameter (mm) | mm | To be specified |  |
| 10 | Unit nominal spacing |  |  |  |
|  | - Tension insulator | mm | 146 |  |
|  | - Suspension insulator | mm | 146 |  |
| 11 | Creepage distance - min | mm | ≥ 440 |  |
| 12 | Total creepage distance | mm | ≥ 6125 |  |
| 13 | Dry power frequency withstand voltage - min. |  |  |  |
|  | Tension insulator | kV | 85 |  |
|  | Suspension insulator | kV | 80 |  |
| 14 | Wet power frequency withstand voltage-min. |  |  |  |
|  | Tension insulator | kV | 50 |  |
|  | Suspension insulator | kV | 50 |  |
| 15 | Lightning impulse withstand |  |  |  |
|  | Tension insulator | kV | 125 |  |
|  | Suspension insulator | kV | 125 |  |
| 16 | Minimum puncture voltage in oil | kV | 130 |  |
| 17 | Zinc sleeve |  | Yes |  |
|  | Insulator set complete |  |  |  |
| 18 | Number of insulator strings in parallel per phase |  |  |  |
| 19 | Min. electro - mechanical failing load complete set |  |  |  |
|  | Type single insulator tension string | kN | 1 x 120 |  |
|  | Type single insulator suspension string | kN | 1 x 70 |  |
| 20 | Number of insulator disk in each string | disk | 16 |  |
| 21 | Overall length of set including clamp and all fittings |  |  |  |
|  | max | mm | To be specified |  |
|  | min | mm | To be specified |  |
| 22 | Weight of complete set with all fittings | kg | To be specified |  |
| 23 | Turnbuckle for 220kV tension insulator |  | yes |  |
| 24 | Arcing horn for 220kV insulator |  | yes |  |
| 25 | Fittings |  |  |  |
|  | - Type of fittings |  | Shackle (socket) coupling (01 point, 22) |  |
| 26 | Requirements for testing (according to item 4.9 & item 4.8) |  | Yes |  |
| 27 | Catalogues |  | To be supplied |  |

110kV Suspension and Tension Insulator

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Insulator unit |  |  |  |
| 1 | Manufacturer/Country of Origin of insulator and Fitting of insulator string |  | To be specified |  |
| 2 | Model type |  |  |  |
|  | Tension insulator |  | U120BP |  |
|  | Suspension insulator |  | U70BLP |  |
| 3 | Insulating material |  | Glass or ceramic |  |
| 4 | Applicable standard |  | IEC 60305 |  |
| 5 | Type of coupling |  | Ball & socket |  |
| 6 | Size of coupling | mm | To be specified |  |
| 7 | Locking device |  | Split pin type |  |
| 8 | Minimum electro-mechanical failing load |  |  |  |
|  | - Tension insulator | kN | ≥ 120 |  |
|  | - Suspension insulator | kN | ≥ 70 |  |
| 9 | Shed diameter (mm) | mm | To be specified |  |
| 10 | Unit nominal spacing |  |  |  |
|  | - Tension insulator | mm | 146 |  |
|  | - Suspension insulator | mm | 146 |  |
| 11 | Creepage distance - min | mm | ≥ 440 |  |
| 12 | Total creepage distance | mm | ≥ 3075 |  |
| 13 | Dry power frequency withstand voltage - min. |  |  |  |
|  | Tension insulator | kV | 85 |  |
|  | Suspension insulator | kV | 80 |  |
| 14 | Wet power frequency withstand voltage-min. |  |  |  |
|  | Tension insulator | kV | 50 |  |
|  | Suspension insulator | kV | 50 |  |
| 15 | Lightning impulse withstand |  |  |  |
|  | Tension insulator | kV | 125 |  |
|  | Suspension insulator | kV | 125 |  |
| 16 | Minimum puncture voltage in oil | kV | 130 |  |
| 17 | Zinc sleeve |  | Yes |  |
|  | Insulator set complete |  |  |  |
| 18 | Number of insulator strings in parallel per phase |  |  |  |
| 19 | Min. electro - mechanical failing load complete set |  |  |  |
|  | Type single insulator tension string | kN | 1 x 120 |  |
|  | Type single insulator suspension string | kN | 1 x 70 |  |
| 20 | Number of insulator disk in each string | disk | 9 |  |
| 21 | Overall length of set including clamp and all fittings |  |  |  |
|  | max | mm | To be specified |  |
|  | min | mm | To be specified |  |
| 22 | Weight of complete set with all fittings | kg | To be specified |  |
| 23 | Turnbuckle for 220kV tension insulator |  | yes |  |
| 24 | Arcing horn for 220kV insulator |  | yes |  |
| 25 | Fittings |  |  |  |
|  | - Type of fittings |  | Shackle (socket) coupling (01 point, 22) |  |
| 26 | Requirements for testing (according to item 4.9 & item 4.8) |  | Yes |  |
| 27 | Catalogues |  | To be supplied |  |

All Aluminium Conductor (AAC-1000; AAC – 800, AAC-630)

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Standard |  | IEC 61089 |  |
|  | Type 1 |  | AAC-1000 |  |
|  | Type 2 |  | AAC - 800 |  |
|  | Type 3 |  | AAC-630 |  |
|  | Nominal cross section area: |  |  |  |
|  | Type 1 | mm2 | 1000 |  |
|  | Type 2 | mm2 | 800 |  |
|  | Type 3 | mm2 | 630 |  |
|  | Stranded number and diameter of strands |  | To be specified |  |
|  | Type 1 | mm | To be specified |  |
|  | Type 2 | mm | To be specified |  |
|  | Type 3 | mm | To be specified |  |
|  | Stranding direction of outer most layer |  | To be specified |  |
|  | Type 1 |  | To be specified |  |
|  | Type 2 |  | To be specified |  |
|  | Type 3 |  | To be specified |  |
|  | Minimum strength load |  | To be specified |  |
|  | Type 1 | kN | ≥160 |  |
|  | Type 2 | kN | ≥ 128 |  |
|  | Type 3 | kN | ≥100.8 |  |
|  | Modulus of elasticity of conductor |  |  |  |
|  | Type 1 | daN/mm2 | To be specified |  |
|  | Type 2 | daN/mm2 | To be specified |  |
|  | Type 3 | daN/mm2 | To be specified |  |
|  | Maximum mass of conductor |  |  |  |
|  | Type 1 | kg/km | 2759 |  |
|  | Type 2 | kg/km | 2207 |  |
|  | Type 3 | kg/km | 1738,3 |  |
|  | Requirements for testing |  | Yes |  |
|  | Continuous current capacity at max. operating temperature of 900C and in air of 250C |  |  |  |
|  | Type 1 | A | To be specified |  |
|  | Type 2 | A | To be specified |  |
|  | Type 3 | A | To be specified |  |
|  | Overall diameter of stranded conductor |  |  |  |
|  | Type 1 | mm | To be specified |  |
|  | Type 2 | mm | To be specified |  |
|  | Type 3 | mm | To be specified |  |
|  | Modulus of elasticity of conductor |  |  |  |
|  | Type 1 | daN/mm2 | To be specified |  |
|  | Type 2 | daN/mm2 | To be specified |  |
|  | Type 3 | daN/mm2 | To be specified |  |
|  | DC resistance at 200C |  |  |  |
|  | Type 1 | Ω/km | ≤ 0,0289 |  |
|  | Type 2 | Ω/km | ≤ 0,0361 |  |
|  | Type 2 | Ω/km | ≤ 0,0458 |  |

HV Connector

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Ordering number |  | To be specified |  |
|  | Applicable standard |  | IEC 694, NEMA CC1 or equivalent |  |
|  | Type |  | Aluminium alloy |  |
|  | Slip strength of bolted connnector |  | To be specified |  |
|  | Bolt and screw of connector |  | Galvanized steel |  |
|  | Short-time withstand current |  |  |  |
|  | + 500kV side | kA/1s | 50 |  |
|  | + 220kV side | kA/1s | 50 |  |
|  | + 110kV side | kA/1s | 40 |  |
|  | Number holes |  | comply |  |
|  | Tightening force for bolt |  |  |  |
|  | - M10 bolt |  | To be specified |  |
|  | - M12 bolt |  | To be specified |  |
|  | - M14 bolt |  | To be specified |  |
|  | - M16 bolt |  | To be specified |  |
|  | Contact grease: |  | Yes |  |
|  | - Manufacturer/Country of Origin |  | To be specified |  |
|  | - Quantity |  | Conformity with connector |  |
|  | Requirements for testing (according to item 4.11) |  | Yes |  |
|  | Catalogue |  | Yes |  |

Important note: For each type of goods specified in the scope of supply and the detailed technical requirements for each type of goods, the Bidder is required to provide a statistic of the test reports of the equipment as required in BD (attached with offered) is described in the following table

LIST OF TEST REPORTS

| No. | Name of equipment | Manufacture/Country of Origin | Name of Laboratory | Name of Equipment | Name of Test | Dated of test/Nam of code | Standard | Evaluated | Remark |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |
| 1 | CIRCUIT BREAKER |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Dielectric test |  |  |  |  |
|  |  |  |  |  | Measurement of the resistance of the main circuit |  |  |  |  |
|  |  |  |  |  | Temperature-rise tests |  |  |  |  |
|  |  |  |  |  | Short-time withstand current and peak withstand current tests |  |  |  |  |
|  |  |  |  |  | Additional tests on auxiliary and control circuits |  |  |  |  |
|  |  |  |  |  | Mechanical and environmental tests |  |  |  |  |
|  |  |  |  |  | Test circuits for short-circuit making and breaking tests |  |  |  |  |
|  |  |  |  |  | TRV at T100; T60; T30; T10 and fault type “Terminal fault”, “Short line fault”, “Out of phase |  |  |  |  |
|  |  |  |  |  | … |  |  |  |  |
| 2 | DISCONNECTOR SWITCH |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Dielectric tests |  |  |  |  |
|  |  |  |  |  | Measurement of the resistance of the main circuits |  |  |  |  |
|  |  |  |  |  | Continuous current tests |  |  |  |  |
|  |  |  |  |  | Short-time withstand current and peak withstand current tests |  |  |  |  |
|  |  |  |  |  | Mechanical endurance test |  |  |  |  |
|  |  |  |  |  | … |  |  |  |  |
| 3 | Current transformers |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Temperature-rise test |  |  |  |  |
|  |  |  |  |  | Impulse voltage withstand test on primary terminals |  |  |  |  |
|  |  |  |  |  | Wet test for outdoor type transformers |  |  |  |  |
|  |  |  |  |  | Electromagnetic Compatibility tests |  |  |  |  |
|  |  |  |  |  | Tests for accuracy |  |  |  |  |
|  |  |  |  |  | Verification of the degree of protection by enclosures |  |  |  |  |
|  |  |  |  |  | Enclosure tightness test at ambient temperature |  |  |  |  |
|  |  |  |  |  | Pressure test for the enclosure |  |  |  |  |
|  |  |  |  |  | Short-time current tests |  |  |  |  |
|  |  |  |  |  | Special tests |  |  |  |  |
| 4 | Capacitor Voltage Transformers |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Temperature-rise test |  |  |  |  |
|  |  |  |  |  | Chopped impulse test |  |  |  |  |
|  |  |  |  |  | Impulse voltage test on primary terminals |  |  |  |  |
|  |  |  |  |  | Wet test for outdoor type transformers |  |  |  |  |
|  |  |  |  |  | Electromagnetic Compatibility tests |  |  |  |  |
|  |  |  |  |  | Test for accuracy |  |  |  |  |
|  |  |  |  |  | Verification of the degree of protection by enclosures |  |  |  |  |
|  |  |  |  |  | Enclosure tightness test at ambient temperature |  |  |  |  |
|  |  |  |  |  | Pressure test for the enclosure |  |  |  |  |
|  |  |  |  |  | Capacitance and tanδ measurement at power frequency |  |  |  |  |
|  |  |  |  |  | Short circuit withstand capability test |  |  |  |  |
|  |  |  |  |  | Ferro-resonance test |  |  |  |  |
|  |  |  |  |  | Transient response test (for protective capacitive transformers) |  |  |  |  |
|  |  |  |  |  | Type tests for carrier frequency accessories |  |  |  |  |
|  |  |  |  |  | Special test |  |  |  |  |
| 5 | TRV Capacitor |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Temperature-rise test |  |  |  |  |
|  |  |  |  |  | Chopped impulse test |  |  |  |  |
|  |  |  |  |  | Impulse voltage test on primary terminals |  |  |  |  |
|  |  |  |  |  | Wet test for outdoor type transformers |  |  |  |  |
|  |  |  |  |  | Electromagnetic Compatibility tests |  |  |  |  |
|  |  |  |  |  | Test for accuracy |  |  |  |  |
|  |  |  |  |  | Verification of the degree of protection by enclosures |  |  |  |  |
|  |  |  |  |  | Enclosure tightness test at ambient temperature |  |  |  |  |
|  |  |  |  |  | Pressure test for the enclosure |  |  |  |  |
|  |  |  |  |  | Capacitance and tanδ measurement at power frequency |  |  |  |  |
|  |  |  |  |  | Short circuit withstand capability test |  |  |  |  |
|  |  |  |  |  | Ferro-resonance test |  |  |  |  |
|  |  |  |  |  | Transient response test (for protective capacitive transformers) |  |  |  |  |
|  |  |  |  |  | Type tests for carrier frequency accessories |  |  |  |  |
|  |  |  |  |  | Special test |  |  |  |  |
| 6 | Surge Arresters |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Insulation withstand tests on the arrester housing |  |  |  |  |
|  |  |  |  |  | Residual voltage test |  |  |  |  |
|  |  |  |  |  | Test to verify long term stability under continuous operating voltage |  |  |  |  |
|  |  |  |  |  | Repetitive charge transfer withstand |  |  |  |  |
|  |  |  |  |  | Heat dissipation behaviour verification of test sample |  |  |  |  |
|  |  |  |  |  | Operating duty test |  |  |  |  |
|  |  |  |  |  | Power-frequency voltage versus time |  |  |  |  |
|  |  |  |  |  | Arrester disconnector/fault indicator (when fitted) |  |  |  |  |
|  |  |  |  |  | Short-circuit tests |  |  |  |  |
|  |  |  |  |  | Bending moment |  |  |  |  |
|  |  |  |  |  | Environmental tests |  |  |  |  |
|  |  |  |  |  | Seal leak rate |  |  |  |  |
|  |  |  |  |  | Radio interference voltage (RIV) |  |  |  |  |
|  |  |  |  |  | Test to verify the dielectric withstand of the internal components of an arrester |  |  |  |  |
|  |  |  |  |  | Test of internal grading components |  |  |  |  |
|  |  |  |  |  | Polluted housing test |  |  |  |  |
| 7 | Post Insulator |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Dry lightning impulse withstand voltage test |  |  |  |  |
|  |  |  |  |  | Wet switching impulse withstand voltage test |  |  |  |  |
|  |  |  |  |  | Wet power frequency withstand voltage test |  |  |  |  |
|  |  |  |  |  | Verification of the dimensions |  |  |  |  |
|  |  |  |  |  | Mechanical failing load test |  |  |  |  |
| 8 | Insulator |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Verification of the dimensions |  |  |  |  |
|  |  |  |  |  | Dry lighting impulse withstand voltage |  |  |  |  |
|  |  |  |  |  | Wet Power frequency withstand voltage |  |  |  |  |
|  |  |  |  |  | Electromechanical failling load test |  |  |  |  |
|  |  |  |  |  | Mechanical failling load test |  |  |  |  |
|  |  |  |  |  | Thermal-mechanical performance test |  |  |  |  |
|  |  |  |  |  | Radio interference voltage test |  |  |  |  |
|  |  |  |  |  | Residual strength test |  |  |  |  |
|  |  |  |  |  | Impulse voltage puncture test |  |  |  |  |
|  |  |  |  |  | Artificial pollution test |  |  |  |  |
|  |  |  |  |  | Power arc tests |  |  |  |  |
|  |  |  |  |  | …. |  |  |  |  |
| 9 | Fittings |  |  |  | IEC 61284 |  |  |  |  |
|  | Tension Clamp |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Mechanical tests |  |  |  |  |
|  |  |  |  |  | Heating cycle test |  |  |  |  |
|  | Spacer Clamp |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Clamp slip test |  |  |  |  |
|  |  |  |  |  | Torsional slip test |  |  |  |  |
|  |  |  |  |  | Clamp bolt tightening test |  |  |  |  |
|  |  |  |  |  | Corona voltage and RIV test |  |  |  |  |
|  | Suspension clamp |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Mechanical tests |  |  |  |  |
|  |  |  |  |  | Slip test |  |  |  |  |
|  | Compression joint |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Mechanical tests |  |  |  |  |
|  |  |  |  |  | Heating cycle test |  |  |  |  |
|  | Accessories of string insulator |  |  |  | Mechanical tests |  |  |  |  |
|  |  |  |  |  | ….. |  |  |  |  |
| 10 | Conductor |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Stress-strain curves |  |  |  |  |
|  |  |  |  |  | Breaking strength of conductor |  |  |  |  |
|  |  |  |  |  | Joints in aluminium wires |  |  |  |  |
|  |  |  |  |  | …… |  |  |  |  |
| 11 | HV terminals connectors |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Temperature rise test |  |  |  |  |
|  |  |  |  |  | Mechanical tensile test |  |  |  |  |
|  |  |  |  |  | Short circuit test |  |  |  |  |
|  |  |  |  |  | Resistance test |  |  |  |  |
|  |  |  |  |  | Radio Interference Voltage (R.I.V) test |  |  |  |  |
| 12 | Lightning wire |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Testing joints on aluminum alloys |  |  |  |  |
|  |  |  |  |  | Testing stress-strain curve. |  |  |  |  |
|  |  |  |  |  | Testing of breaking force of cable. |  |  |  |  |
|  |  |  |  |  | Creep test |  |  |  |  |

III. Reference Drawings