### SECTION V.2 TECHNICAL SPECIFICATIONS

CLAUSE V.2.2: TECHNICAL SPECIFICATIONS AND DATA SHEETS

TABLE OF CONTENTS

SECTION V.3 TECHNICAL DATA SHEETS	2

1.	500 KV CIRCUIT BREAKERS FOR LINE BAYS AND TRANSFORMER BAYS		3

2.	500 KV REACTOR CIRCUIT BREAKERS	10

3.	220KV CIRCUIT BREAKER	17

4.	35KV CIRCUIT BREAKER	22

5.	500KV DISCONNECTOR AND EARTHING SWITCH	26

6.	220KV DISCONNECTOR AND EARTHING SWITCH	32

7.	110KV DISCONNECTOR AND EARTHING SWITCH	37

8.	35 KV DISCONNECTOR AND EARTHING SWITCH	42

9.	500KV CURRENT TRANSFORMER	45

10.	220KV CURRENT TRANSFORMER	47

11.	35KV CURRENT TRANSFORMER	50

13.	500KV CAPACITOR VOLTAGE TRANSFORMER	54

14.	220KV CAPACITOR VOLTAGE TRANSFORMER	57

15.	35KV INDUCTIVE VOLTAGE TRANSFORMER	60

16.	500KV SURGE ARRESTER	64

17.	220KV SURGE ARRESTER	66

19.	110KV SURGE ARRESTER	68

20.	35KV SURGE ARRESTER	70

21.	500KV POST INSULATOR	72

22.	220KV POST INSULATOR	74

23.	110KV POST INSULATOR	76

24.	35KV POST INSULATOR	78

25.	123KV NEUTRAL GROUDING REACTOR	80

26.	NEUTRAL RESISTOR CONNECTED NEUTRAL REACTORS	82

27.	500KV TRV CAPACITOR	84

28.	500KV SUSPENSION AND TENSION INSULATOR	86

29.	220KV SUSPENSION AND TENSION INSULATOR	88

30.	MALLEABLE ALUMINIUM ALLOY TUBE (E-AL MGSI 0.5F22)	90

31.	ALL ALUMINIUM CONDUCTOR (AAC-1000; AAC-800; AAC-630)	91

32.	LIGHTNING WIRES (PHLOX 116)	93

33.	35KV – AC-XLPE 2.5/PVC – 300MM2	95

34.	HV CONNECTOR	96

- SECTION V.3 TECHNICAL DATA SHEETS

- The Data in the “Required” column of the following tables are to be read in conjunction with the descriptions in the technical specifications, and are requirements which the Supplier has to fulfill.

- If there is any deviation from description of equipment and materials item of technical specifications, the data of this item (Data sheets) shall to be used.

- The Bidder shall copy the following data sheets, completely fill in the "Tendered" column, and include them in his Bid. Each data sheet shall be initialled by the Bidder.

- Where the space in the "Tendered" Column is not sufficient to enter Bidder's information, a reference shall be made to separate sheets which are to be attached at the end of the section. Such additional sheets shall contain the specific information and data. References to general leaflets, catalogues etc. are not acceptable and may be evaluated as missing information.

- 500 kV circuit breakers for line bays and transformer bays

| Item No | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 62271-100, IEC 62271-1 |  |
|  | Frequency | Hz | 50 |  |
|  | Method of neutral grounding |  | Directly earthed |  |
|  | Type |  | Outdoor, live tank, single phase (three phases operation), SF6 insulated, single pressure (puffer) type |  |
|  | Nominal voltage | kV | 500 |  |
|  | Max operator voltage | kV | 550 |  |
|  | Rated voltage | kV | ≥ 550 |  |
|  | Rated short-duration power-frequency withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV | 620 800 620 |  |
|  | Rated Lightning impulse (1.2/50µs) withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV peak | ≥1550 1550(+315) 1550 |  |
|  | Rated switching impulse withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV | ≥1175 900(+450) 1760 |  |
|  | TRV peak values of transient recovery voltage |  | Comply to IEC 62271-100 |  |
|  | Test duty T10 |  |  |  |
|  | + TRV peak value | kV | To be specified |  |
|  | + Rate-of-rise | kV/µs | To be specified |  |
|  | Test duty T30 |  |  |  |
|  | + TRV peak value | kV | To be specified |  |
|  | + Rate-of-rise | kV/µs | To be specified |  |
|  | Test duty T60 |  |  |  |
|  | + TRV peak value | kV | To be specified |  |
|  | + Rate-of-rise | kV/µs | To be specified |  |
|  | Test duty T100 |  |  |  |
|  | + TRV peak value | kV | To be specified |  |
|  | + Rate-of-rise | kV/µs | To be specified |  |
|  | Test duty OP1 - OP2 |  |  |  |
|  | + TRV peak value | kV | Comply to IEC 62271-100 |  |
|  | + Rate-of-rise | kV/µs | Comply to IEC 62271-100 |  |
|  | Rated normal current | A | ≥ 3150A |  |
|  | Rated short time withstand current | kA rms. | ≥ 50 |  |
|  | Rated duration of short-circuits | sec | ≥ 1 |  |
|  | Rated peak withstand current | kA peak | ≥ 125 |  |
|  | Rated line – charging breaking current | Arms | ≥ 500 |  |
|  | Rate cable – charging breaking current | Arms | 500 |  |
|  | Rated capacitive breaking current | Arms | 400 |  |
|  | % DC component of short-circuit breaking current |  | To be specified |  |
|  | Resistance of main contact (new contact) | µΩ | To be specified |  |
|  | Operating mechanism drive type |  | Spring (There is a charge indicator, both manual and motor) |  |
|  | Maximum noise level according to IEC62271-37-082 when the circuit breaker is in operation | dB | To be specified |  |
|  | On/Off Indicator |  | Yes |  |
|  | Operating mechanism |  | Single pole |  |
|  | Manufacturer’s name |  | To be specified |  |
|  | Country of origin |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Mechanical operation duration | Times | 10,000 |  |
|  | Number of times of switching (closing-opening) of rated current | Times | 2500 |  |
|  | Number of operation with short circuit current is 50% of rating | Times | 30 |  |
|  | Number of operation with short circuit current is 100% of rating | Times | 10 |  |
|  | Opening time | ms | ≤ 40 |  |
|  | Closing time | ms | ≤120 |  |
|  | Open-close time of 3 phases not simultaneously | ms | ≤4 |  |
|  | Rated Operating Sequence |  | O-0.3sec.-CO -3min -CO |  |
|  | Minimum Clearance: |  |  |  |
|  | Between phases | mm | ≥ 7400 |  |
|  | Between phase and earth | mm | ≥ 4100 |  |
|  | Porcelain insulator: |  |  |  |
|  | - Applicable standard |  | According to IEC 62155 or equivalent |  |
|  | - Material |  | Brown porcelain |  |
|  | - Minimum nominal creepage distance | mm/kV | 31 |  |
|  | - Total creepage distance | mm | To be specified |  |
|  | Maximum impact load when the circuit breaker is in operation, kN | kN | To be specified |  |
|  | Circuit Breaker terminal load capacity, kN | kN | To be specified |  |
|  | Chamber system, bushing: |  |  |  |
| - | There is a dehumidifier, decomposition product and pressure release unit rising inside |  | Comply |  |
| - | Links between the pole or other parts with bolts |  | Comply |  |
|  | There is an corona ring to ensure the voltage balance between pole |  | yes |  |
|  | Interrupting and arcing chamber |  |  |  |
|  | Structure of the Interrupting and arcing chamber |  | live tank |  |
|  | Quantity of interrupting chamber per one pole. |  | ≥02 |  |
|  | First-pole-to-clear factor | pu | 1.3 |  |
|  | Terminal fault Short-line fault Out-of-phase reverse fault |  | 1.3 1 2 |  |
|  | Insulating medium |  | SF6 |  |
|  | Grading capacitor (is installed parallel with chamber) |  | To be specified (Depending on the calculation and technological solutions of the manufacturer, Offer circuit breaker may or may not be equipped with the grading capacitor. However, the circuit breaker needs to meet the TRV, RRRV values ​​required in the bidding document and other requirements specified in IEC 62271-100) |  |
|  | The number of grading capacitor for each phase (if any) |  | ≥2 |  |
|  | Number of closing coil |  | 1 coil/phase |  |
|  | Number of tripping coil |  | 2 coil /phase |  |
|  | Number of auxiliary contacts for 1 phase |  |  |  |
|  | Normally opened |  | 12 NO |  |
|  | Normally closed |  | 12 NC |  |
|  | SF6 gas |  |  |  |
|  | The meter indicates gas density |  | - Temperature compensation type - 03 meter for 3 phases. - There are SF₆ gas alarm circuits with level 1 and level 2. |  |
|  | One way valve for charge (discharge) SF6 |  | Yes |  |
|  | Leakage of SF6 per year | %/year | ≤ 0.5 |  |
|  | Purity of SF6 | % | ≥ 98,5% V |  |
|  | Dew-point temperature | oC | Comply with IEC 60376 |  |
|  | SF6 mass for one three-pole circuit breaker | kg | To be specified |  |
|  | Rated SF6 density | kg/m3 | To be specified |  |
|  | Threshold gas density SF 6 level 1 | kg/m3 | To be specified |  |
|  | Threshold gas density SF 6 level 2 | kg/m3 | To be specified |  |
|  | Local control cabinet: |  |  |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Material of cabinet |  | Aluminium alloy or stainless steel |  |
|  | Protection class |  | IP55 |  |
|  | Minimum thickness of cabinet, mm |  | ≥2 |  |
|  | Full device and accessories for operational in “local” and “remote” mode |  | Yes |  |
|  | Mechanical opening/ closing operations |  | Yes |  |
|  | Operating counter |  | Yes |  |
|  | Other functions circuit (trip coil supervision circuit, power state of circuit, springs charged circuit…) |  | Yes |  |
|  | Anti-pumping circuit |  | Yes |  |
|  | Non-synchronous protection circuit |  | Yes |  |
|  | Overcurrent and overload protection circuit for the motor |  | Yes |  |
|  | Spring charge indicator |  | Yes |  |
|  | System heating and lighting with LED lights, MCB |  | Yes |  |
|  | Spring charge |  | Spring charge (Motor and manual drive) |  |
|  | Maximum spring charge time | s | 15 |  |
|  | Steel supporting structure |  |  |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Material |  | Hot dip galvanized |  |
|  | Auxiliary supply voltage: |  |  |  |
|  | Motor Recommend using an additional 220 VAC source: 220 (+10%; -15%) | VDC and VAC | 220 (+10%; -15%) |  |
|  | Trip coil | VDC | 220 (+10%; -30%) |  |
|  | Close coil | VDC | 220 (+10%; -25%) |  |
|  | Heating and Lighting | VAC | 220 (+10%; -15%) |  |
|  | Maximum power trip coil or close coil for all 3 phases | VA | 1200 |  |
|  | HV terminal: |  |  |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Materials |  | Aluminum alloy |  |
|  | Dimensions |  | To be specified |  |
|  | Number of holes |  | To be specified |  |
|  | Size of holes |  | To be specified |  |
|  | Spacing of holes |  | To be specified |  |
|  | Bolts |  | Stainless Steel |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes The Bidder shall be filled list of test report as shown in item 2.21 |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 1677/QĐ-EVNNPT date 24/08/2025 |  | Yes |  |

Values of prospective transient recovery voltage (**)

| Rated voltage Ur (kV) | Test-duty | First-pole-to-clear factor kpp (p.u) | Amplitude factor kaf (p.u) | First reference voltage u1 (kV) | Time t1 (s) | TRV peak value uc (kV) | Time t2 or t3 (s) | Time delay td (s) | Voltage u’ (kV) | Time t’(s) | Rate of rise u1/t1 uc/t3 (kV/s) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 550 | T100 |  |  |  |  |  |  |  |  |  |  |
|  | T60 |  |  |  |  |  |  |  |  |  |  |
|  | T30 |  |  |  |  |  |  |  |  |  |  |
|  | T10 |  |  |  |  |  |  |  |  |  |  |

Values of transient recovery voltage

| Rated voltage Ur (kV) | Type of Test | First-pole-to-clear factor kpp (p.u) | Amplitude factor kaf (p.u) | First reference voltage u1 (kV) | Time t1 (s) | TRV peak value uc (kV) | Time t2 or t3 (s) | Time delay td (s) | Voltage u’ (kV) | Time t’(s) | Rate of rise of recovery voltage u1/t1 (kV/s) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 550 | Terminal fault |  |  |  |  |  |  |  |  |  |  |
|  | Short-line fault |  |  |  |  |  |  |  |  |  |  |
|  | Out-of-phase |  |  |  |  |  |  |  |  |  |  |

(*) The bidder must provide documents of TRV obtained from the above test duties (T10, T30, T60, T100).

- 220kV Circuit Breaker

| Item No | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Model type |  | To be specified |  |
|  | Applicable standard |  | IEC 62271-100, IEC 62271-1 |  |
|  | Frequency | Hz | 50 |  |
|  | Method of neutral grounding |  | Directly earthed |  |
|  | Type |  | Outdoor, live tank, single phase (three phases operation), SF6 insulated, single pressure (puffer) type |  |
|  | Nominal voltage | kV | 220 |  |
|  | Max operator voltage | kV | 242 |  |
|  | Rated voltage | kV | ≥245 |  |
|  | Rated short-duration power-frequency withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV | 460 |  |
|  | Rated Lightning impulse (1.2/50µs) withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV peak | 1050 |  |
|  | TRV peak values of transient recovery voltage, kV + Terminal fault + Short-line fault + Out-of-Phase | kV | 364 280 500 |  |
|  | Rated current |  | ≥ 4000 A (transformer, coupler, transfer, busbar section, Nam Dinh 3 bays) ≥ 2000 A (other line bay) |  |
|  | Rated short-time withstand current | kA rms. | ≥ 50 |  |
|  | Rated duration of short-circuits | sec | ≥ 1 |  |
|  | Rated peak withstand current | kA peak | ≥ 125 |  |
|  | Rated line – charging breaking current | Arms | ≥ 125 |  |
|  | Rate cable – charging breaking current | Arms | 250 |  |
|  | Rated capacitive breaking current | Arms | 400 |  |
|  | % DC component of short-circuit breaking current |  | To be specified |  |
|  | Resistance of main contact | µΩ | To be specified |  |
|  | Operating mechanism drive type |  | Spring (There is a charge indicator, both manual and motor) |  |
|  | Maximum noise level according to IEC62271-37-082 when the circuit breaker is in operation | dB | To be specified |  |
|  | On/Off Indicator |  | Yes |  |
|  | Operating mechanism |  | Single pole |  |
|  | Manufacturer’s name |  | To be specified |  |
|  | Country of origin |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Mechanical operation duration | Times | 10,000 |  |
|  | Number of operation at 100% rated current | Times | 2500 |  |
|  | Number of operation with short circuit current is 50% of rating | Times | 30 |  |
|  | Number of operation with short circuit current is 100% of rating | Times | 10 |  |
|  | Opening time | ms | ≤ 35 |  |
|  | Closing time | ms | To be specified |  |
|  | Open-close time of 3 phases not simultaneously | ms | ≤4 |  |
|  | Rated Operating Sequence |  | O-0.3sec.-CO -3min -CO |  |
|  | Minimum Clearance: |  |  |  |
|  | Between phases | mm | ≥ 2100 |  |
|  | Between phase and earth | mm | ≥ 2100 |  |
|  | Porcelain insulator: |  |  |  |
|  | - Applicable standard |  | According to IEC 62155 or equivalent |  |
|  | - Material |  | Brown porcelain |  |
|  | - Minimum nominal creepage distance | mm/kV | 31 |  |
|  | - Total creepage distance | mm | To be specified |  |
|  | Maximum impact load when the circuit breaker is in operation, kN | kN | To be specified |  |
|  | Circuit Breaker terminal load capacity, kN | kN | To be specified |  |
|  | Chamber system, bushing: |  |  |  |
| - | There is a dehumidifier, decomposition product and pressure release unit rising inside |  | Comply |  |
| - | Links between the pole or other parts with bolts |  | Comply |  |
|  | Interrupting and arcing chamber |  |  |  |
|  | Structure of the Interrupting and arcing chamber |  | live tank |  |
|  | Quantity of interrupting chamber per one pole. |  | 01 |  |
|  | First-pole-to-clear factor | pu | 1.3 |  |
|  | Terminal fault Short-line fault Out-of-phase reverse fault |  | 1,3 1 2 |  |
|  | Insulating medium |  | SF6 |  |
|  | Number of closing coil |  | 1 coil/phase |  |
|  | Number of tripping coil |  | 2 coil /phase |  |
|  | Number of auxiliary contacts for 1 phase |  |  |  |
|  | Normally opened |  | 12 NO |  |
|  | Normally closed |  | 12 NC |  |
|  | SF6 gas |  |  |  |
|  | The meter indicates gas density |  | - Temperature compensation type - 03 meter for 3 phases. Gas alarm circuit level 1 (alarm), level 2 (alarm and operating lock) |  |
|  | One way valve for charge (discharge) SF6 |  | Yes |  |
|  | Leakage of SF6 per year | %/year | ≤ 0.5 |  |
|  | Purity of SF6 | % | ≥ 98,5% V |  |
|  | Dew-point temperature | oC | Comply with IEC 60376 |  |
|  | SF6 mass for one three-pole circuit breaker | kg | To be specified |  |
|  | Rated SF6 density | kg/m3 | To be specified |  |
|  | Threshold gas density SF 6 level 1 | kg/m3 | To be specified |  |
|  | Threshold gas density SF 6 level 2 | kg/m3 | To be specified |  |
|  | Local control cabinet: |  |  |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Material of cabinet |  | Aluminium alloy or stainless steel |  |
|  | Protection class |  | IP55 |  |
|  | Minimum thickness of cabinet, mm |  | ≥2 |  |
|  | Full device and accessories for operational in “local” and “remote” mode |  | Yes |  |
|  | Mechanical opening/ closing operations |  | Yes |  |
|  | Operating counter |  | Yes |  |
|  | Other functions circuit (trip coil supervision circuit, power state of circuit, springs charged circuit…) |  | Yes |  |
|  | Anti-pumping circuit |  | Yes |  |
|  | Non-synchronous protection circuit |  | Yes |  |
|  | Overcurrent and overload protection circuit for the motor |  | Yes |  |
|  | Spring charge indicator |  | Yes |  |
|  | System heating and lighting with LED lights, MCB |  | Yes |  |
|  | Spring charge |  | Spring charge (Motor and manual drive) |  |
|  | Maximum spring charge time | s | 15 |  |
|  | Steel supporting structure |  |  |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Material |  | Hot dip galvanized |  |
|  | Auxiliary supply voltage: |  |  |  |
|  | Motor Recommend using an additional 220 VAC source: 220 (+10%; -15%) | VDC and VAC | 220 (+10%; -15%) |  |
|  | Close coil | VDC | 220 (+10%; -25%) |  |
|  | Trip coil | VDC | 220 (+10%; -30%) |  |
|  | Heating and Lighting | VAC | 220 (+10%; -15%) |  |
|  | Maximum power trip coil or close coil for all 3 phases | VA | 1200 |  |
|  | HV terminal: |  |  |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Materials |  | Aluminum alloy |  |
|  | Dimensions |  | To be specified |  |
|  | Number of holes |  | To be specified |  |
|  | Size of holes |  | To be specified |  |
|  | Spacing of holes |  | To be specified |  |
|  | Bolts |  | Stainless Steel |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes The Bidder shall be filled list of test report as shown in item 2.21 |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 1677/QĐ-EVNNPT date 24/08/2025 and 2416/QĐ-EVNNPT date 09/12/2025. |  | Yes |  |

- 35kV Circuit Breaker

| Item No | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 62271-100 |  |
|  | Type |  | Outdoor, live tank, three poles, SF6 or Vacuum insulated, single pressure (puffer) type |  |
|  | Insulating medium |  | SF6 or Vacuum |  |
|  | Dead or live tank construction |  | Live tank |  |
|  | Nominal voltage | kV | 35 |  |
|  | Rated voltage | kV | 38,5 |  |
|  | Rated current | A | ≥ 630 |  |
|  | Frequency | Hz | 50 |  |
|  | Rated three phase symmetrical short-circuit breaking current | kA rms. | ≥ 25 |  |
|  | Rated peak withstand current | kA peak | ≥ 62.5 |  |
|  | Rated duration of short-circuits | sec | ≥ 1 |  |
|  | Rated Operating Sequence |  | O-0.3sec.-CO -3min -CO |  |
|  | Rated Lightning impulse (1.2/50µs) withstand voltage | kV peak | ≥ 185 |  |
|  | Rated short-duration power-frequency withstand voltage | kV rms. | ≥ 80 |  |
|  | Rated first-pole-to-clear factor |  | 1.5 |  |
|  | Resistance of main contact (new contact) | µΩ | To be specified |  |
|  | Chamber system, pole center of CB |  | - There are dehumidifiers, decomposition products and high pressure release parts inside; - Links between the pole or other parts with bolts; |  |
|  | Porcelain insulator: |  |  |  |
| - | Applicable standard |  | According to IEC 62155 or equivalent |  |
| - | Material |  | Brown porcelain |  |
| - | Minimum nominal creepage distance | mm/kV | ≥ 31 |  |
| - | Total creepage distance | mm | To be specified |  |
| - | Maximum impact load when the circuit breaker is in operation, kN | kN | To be specified |  |
|  | Circuit Breaker terminal load capacity, kN | kN | To be specified |  |
|  | Mechanical operation duration | times | ≥ 10,000 |  |
|  | Operation with rate current duration | times | ≥ 2,500 |  |
|  | Total trip time with 3 phases short-circuit (not overhaul) | times | ≥ 20 |  |
|  | Operating mechanism drive type |  | Spring (There is a charge indicator, both manual and motor) |  |
|  | Protection class of operating control cabinet |  | IP55 |  |
| - | Open time | ms | ≤ 60 |  |
| - | Close time | ms | To be specified |  |
|  | Operating counter |  | Yes |  |
|  | Number of spare auxiliary contacts (Repeating aux. switch contact via aux. contactor or aux. relay shall be not accepted) |  |  |  |
| - | Normally open |  | ≥ 06 |  |
| - | Normally closed |  | ≥ 06 |  |
|  | Number of closing coil |  | 1 coil/phase |  |
|  | Number of tripping coil |  | ≥1 coil/phase |  |
|  | Total weight of complete circuit breaker | kg | To be specified |  |
|  | SF6 gas (Applicable to SF6 gas circuit breaker) |  |  |  |
| - | The meter indicates gas density |  | - Temperature compensation type - 01 meter for 3 phases. - Gas alarm circuit level 1 (alarm), level 2 (alarm and operating lock) |  |
|  | Pressure relief device for SF6 gas |  | Yes |  |
|  | Leakage of SF6 per year | %/year | ≤ 0.5 |  |
|  | Purity of SF6 | % | ≥ 98,5% V |  |
|  | Dew-point temperature | oC | Comply with IEC 60376 |  |
|  | SF6 mass for one three-pole circuit breaker | kg | To be specified |  |
|  | Rated SF6 density | kg/m3 | To be specified |  |
|  | Threshold gas density SF 6 level 1 | kg/m3 | To be specified |  |
|  | Threshold gas density SF 6 level 2 | kg/m3 | To be specified |  |
|  | Local control cabinet |  |  |  |
| - | Manufacturer/Country of Origin |  | To be specified |  |
| - | Place of factory |  | To be specified |  |
| - | Designation |  | To be specified |  |
| - | Material of cabinet |  | Aluminium alloy (Al Mg3 H22) or stainless steel (Inox-304) |  |
| - | Protection class |  | IP55 (IEC 60529) |  |
| - | Parameter table |  | Made of rust-proof material and lettering that will not fade over the life of the cutter |  |
| - | Anti-pumping circuit |  | Yes |  |
| - | Other functions circuit (trip coil supervision circuit, power state of ATM circuit, uncharged springs circuit…) |  | Yes |  |
| - | Local/Remote switches |  | Yes |  |
| - | Mechanical opening / closing operations |  | Yes |  |
| - | Heating/Lighting system |  | Yes |  |
| - | Operating counter |  | Yes |  |
| - | Full set of Other auxiliary equipment |  | Yes |  |
| - | Power terminals and Tripping terminals must be separated and have at least 01 blank terminal between them. |  | Required |  |
|  | Auxiliary supply voltage: |  |  |  |
| - | Motor | VDC | 220 (+10%; -15%) |  |
|  | Close coil | VDC | 220 (+10%; -15%) |  |
|  | Trip coil | VDC | 220 (+10%; -30%) |  |
|  | Heating and Lighting | VAC | 220 (+10%; -15%) |  |
|  | Steel supporting structure |  |  |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Material |  | Hot dip galvanized |  |
|  | HV terminal: |  |  |  |
| - | Manufacturer/Country of Origin/ Address |  | To be specified |  |
| - | Materials |  | Aluminum alloy |  |
| - | Dimensions |  | To be specified |  |
|  | Bolts |  | Stainless Steel |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes The Bidder shall be filled list of test report as shown in item 2.21 |  |
|  | Energize the spring manually |  | Yes |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 272/QĐ-EVN date 24/7/2019 |  | Yes |  |

- 500kV Disconnector and Earthing switch

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
| 1 | Applicable standard |  | IEC 62271-102 |  |
| 2 | Rated frequency, Hz |  | 50 |  |
| 3 | Method of neutral grounding |  | Directly earthed |  |
| 4 | Type |  | outdoor |  |
| 4.1 | Structure of one set |  | single phase |  |
| 4.2 | Break type |  | Vertical break, knee type |  |
| 4.3 | Number of earthing switches can be equipped for disconnector |  | (0, 1, 2) earthing blade |  |
| 5 | Voltage parameters |  |  |  |
| 5.1 | System voltage | kV | 500 |  |
| 5.2 | Maximum voltage | kV | 550 |  |
| 5.3 | Rated voltage | kV | 550 |  |
| 5.4 | Rated short-duration power-frequency withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV | 620 800 620 |  |
| 5.5 | Rated lightning impulse withstand voltage (1,2/50 µs-BIL) + Phase-to-Earth + Across the isolating distance + Between phases | kV peak | ≥1550 ≥1550 (+315) ≥1550 |  |
| 5.6 | Rated switching impulse voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV peak | ≥1175 ≥900 (+450) ≥1760 |  |
| 6 | Current parameters |  |  |  |
| 6.1 | Rated normal current Ir | A | 3150A |  |
| 6.2 | Rated short-time withstand current | kA rms | ≥50 |  |
| 6.3 | Rated duration of short-circuit | s | ≥1 |  |
| 6.4 | Rated peak withstand current | kA peak | ≥125 |  |
| 7 | Main circuit contact resistance | µΩ | To be specified |  |
| 8 | Earthing switch parameters |  |  |  |
| 8.1 | Rated short-circuit making current | kA | ≥50 |  |
| 8.2 | Rated induced current of electrostatic coupling | A rms | 25 (applied for ES of transmission line side at outgoing bays) |  |
| 8.3 | Rated induced current of electromagnetic coupling | A rms | 160 (applied for ES of transmission line side at outgoing bays) |  |
| 8.4 | Rated withstand voltage between insulated terminals and bases earthed | kV | ≥ 635 |  |
| 9 | Operational capabilities of disconnector, earthing switch |  |  |  |
| 9.1 | Drive mechanism |  | Single phase |  |
| 9.2 | Mechanical endurance class |  |  |  |
| - | Disconnector |  | M1 |  |
| - | Earthing switch |  | M0 |  |
| 9.3 | Total mechanical operating, no maintenance |  |  |  |
| - | Disconnector | times | ≥2000 |  |
| - | Earthing switch | times | ≥1000 |  |
| 9.4 | Operated lever |  | yes |  |
| 9.5 | Mechanical interlock (Disconnector and Earthing switch) |  | yes |  |
| 10 | Total weight | kg | To be specified |  |
| 11 | Required clearance |  |  |  |
| 11.1 | Phase to phase | mm | ≥ 6100 (or switching impulse response 1760 kV peak) |  |
| 11.2 | Phase to earth | mm | ≥ 4100 (or switching impulse response 1175 kV peak) |  |
| 12 | Poles post of disconnector |  |  |  |
| 12.1 | Applicable standard |  | IEC 60273 or equivalent |  |
| 12.2 | Material |  | Brown ceramic porcelain |  |
| 12.3 | Minimum creepage distance | mm/ kV | ≥ 31 |  |
| 12.4 | Total creepage distance | mm | To be specified |  |
| 12.5 | Withstand the impact loads of disconnector - Three phase disconnector/Earthing switch + Straight load Fa1, Fa2, kN + Cross load Fb1, Fb2, kN - Single phase disconnector/Earthing switch + Straight load Fa1, Fa2, kN + Cross load Fb1, Fb2, kN - Vertical Force, Fc - Vertical Force, Fc, kN | kN | 1.6: Ir≤3150A 2.0: Ir>3150A 0.53: Ir≤3150A 0.66: Ir>3150A 2.0: Ir≤3150A 4.0: Ir>3150A 0.8: Ir≤3150A 1.6: Ir>3150A 1.5 |  |
| 12.6 | Maximum impact load when the disconnector operates | kN | To be specified |  |
| 12.7 | Minimum distance in static condition: - Between phase and earth | mm | 4100 |  |
|  | - Between phases, mm | mm | 4100 |  |
| 13 | Material of main contact |  | Copper, Copper alloy or silver/nickel plated aluminum alloy |  |
| 14 | Operating mechanism |  |  |  |
| 14.1 | Disconnector |  | Manual and/or electrical motor |  |
| 14.2 | Earthing switch |  | Manual and/or electrical motor |  |
| 15 | Local control cabinet of disconnector, earthing switch: |  |  |  |
| 15.1 | Cabinet enclosure material |  | Aluminum alloy or stainless steel (Inox 304) or galvanized steel and the cabinet surface can be painted suitable to requirements |  |
| 15.2 | Minimum protection class |  | IP55 |  |
| 15.3 | Minimum thickness of cabinet enclosure | mm | ≥2 |  |
| 15.4 | Limit switch contact of disconnector |  | ≥(3NO+3NC) |  |
| 15.5 | Auxiliary switch contact of disconnector |  | ≥(12NO+12NC) |  |
| 15.6 | Auxiliary switch contact of earthing switch |  | ≥(10NO+10NC) |  |
| 15.7 | Rated DC current of the auxiliary contact | A | 10 |  |
| 15.8 | DC current withstands short-time of the auxiliary contact |  | 100 A/30 ms |  |
| 15.9 | Selection switch of Local/Remote |  | yes |  |
| 15.10 | "Open/Close" push buttons of disconnector, earthing switch |  | yes |  |
| 15.11 | Motor and MCBs with auxiliary contacts have separate power supply |  | yes |  |
| 15.12 | Overcurrent and overload protection for the motor |  | yes |  |
| 15.13 | Drying system with temperature sensor, led lighting, drying and lighting have separate power supply by MCBs with auxiliary contacts |  | yes |  |
| 15.14 | Electrical interlock circuit between disconnector and earthing switch |  | yes |  |
| 16 | Supply voltage: |  |  |  |
| 16.1 | Motor | VDC | 220 (+10%; -15%) |  |
| 16.2 | Trip and Close | VDC | 220 (+10%; -15%) |  |
| 16.3 | Heating and Lighting | VAC | 220 (+10%; -15%) |  |
| 17 | Material of support structures for disconnector |  | Galvanized steel |  |
| 18 | HV terminals: |  |  |  |
| 18.1 | Materials |  | Aluminum alloy /copper |  |
| 18.2 | Dimensions |  | suitable for conductor |  |
| 18.3 | Bolt |  | Stainless steel |  |
| 19 | Catalogues |  | To be supplied |  |
| 20 | Requirements for testing (according to Technical Specification) |  | Yes The Bidder shall be filled list of test report as shown in item 2.21 |  |
| 21 | The remaining parameters or different will comply with the provisions of 1676/QĐ-EVNNPT date 24/08/2025 |  | Yes |  |

- 220kV Disconnector and Earthing switch

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
| 1 | Applicable standard |  | IEC 62271-102 |  |
| 2 | Rated frequency, Hz |  | 50 |  |
| 3 | Method of neutral grounding |  | Directly earthed |  |
| 4 | Type |  | outdoor |  |
| 4.1 | Structure of one set |  | single phase/three phase |  |
| 4.2 | Break type |  | horizontal break |  |
| 4.2 | Number of earthing switches can be equipped for disconnector |  | (0, 1, 2) earthing blade |  |
| 5 | Voltage parameters |  |  |  |
| 5.1 | System voltage | kV | 220 |  |
| 5.2 | Maximum voltage | kV | 242 |  |
| 5.3 | Rated voltage | kV | 245 |  |
| 5.4 | Rated short-duration power-frequency withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV | 460 530 460 |  |
| 5.5 | Rated lightning impulse withstand voltage (1,2/50 µs-BIL) + Phase-to-Earth + Across the isolating distance + Between phases | kV peak | 1050 1200 1050 |  |
| 6 | Current parameters |  |  |  |
| 6.1 | Rated normal current Ir | A | ≥ 4000 A (transformer, coupler, transfer, busbar section, Nam Dinh 3 bays) ≥ 2000 A (other line bay) |  |
| 6.2 | Rated short-time withstand current | kA rms | ≥50 |  |
| 6.3 | Rated duration of short-circuit | s | ≥1 |  |
| 6.4 | Rated peak withstand current | kA peak | ≥125 |  |
| 7 | Main circuit contact resistance | µΩ | To be specified |  |
| 8 | Earthing switch parameters |  |  |  |
| 8.1 | Rated short-circuit making current | kA | 50 |  |
| 8.2 | Rated induced current of electrostatic coupling | A rms | 3 |  |
| 8.3 | Rated induced current of electromagnetic coupling Rated induced current of electromagnectic coupling | A rms | 80 |  |
| 8.4 | Rated withstand voltage between insulated terminals and bases earthed | kV | ≥283 |  |
| 9 | Operational capabilities of disconnector, earthing switch |  |  |  |
| 9.1 | Drive mechanism |  | Single phase/ three phase |  |
| 9.2 | Mechanical endurance class |  |  |  |
| - | Disconnector |  | M1 |  |
| - | Earthing switch |  | M0 |  |
| 9.3 | Total mechanical operating, no maintenance |  |  |  |
| - | Disconnector | times | ≥2000 |  |
| - | Earthing switch | times | ≥1000 |  |
| 9.4 | Operated lever |  | yes |  |
| 9.5 | Mechanical interlock (Disconnector and Earthing switch) |  | yes |  |
| 10 | Total weight | kg | To be specified |  |
| 11 | Required clearance |  |  |  |
| 11.1 | Phase to phase | mm | ≥ 2100 |  |
| 11.2 | Phase to earth | mm | ≥ 2100 |  |
| 12 | Poles post of disconnector |  |  |  |
| 12.1 | Applicable standard |  | IEC 60273 or equivalent |  |
| 12.2 | Material |  | Brown ceramic porcelain |  |
| 12.3 | Minimum creepage distance | mm/ kV | ≥31 |  |
| 12.4 | Total creepage distance | mm | To be specified |  |
| 12.5 | Withstand the impact loads of disconnector - Three phase disconnector/Earthing switch + Straight load Fa1, Fa2, kN + Cross load Fb1, Fb2, kN - Single phase disconnector/Earthing switch + Straight load Fa1, Fa2, kN + Cross load Fb1, Fb2, kN - Vertical Force, Fc, kN | kN | 0.8: Ir≤2500A 1.0: Ir>2500A 0.27: Ir≤2500A 0.33:Ir>2500A 1.25: Ir≤2500A 1.6: Ir>2500A 0.4: Ir≤2500A 0.5: Ir>2500A 1.25 |  |
| 12.6 | Maximum impact load when the disconnector operates | kN | To be specified |  |
| 12.7 | Minimum distance in static condition: - Between phase and earth | mm | ≥ 2100 |  |
|  | - Between two poles/phase | mm | ≥ 2100 |  |
|  | - Center-to-center distance of the two porcelain insulators/phase | mm | ≤ 2700 (Suitable for the bay arrangement) |  |
| 13 | Material of main contact |  | Copper, Copper alloy or silver/nickel plated aluminum alloy |  |
| 14 | Operating mechanism |  |  |  |
| 14.1 | Disconnector |  | Manual and/or electrical motor |  |
| 14.2 | Earthing switch |  | Manual and/or electrical motor |  |
| 15 | Local control cabinet of disconnector, earthing switch: |  |  |  |
| 15.1 | Cabinet enclosure material |  | Aluminum alloy or stainless steel (Inox 304) or galvanized steel and the cabinet surface can be painted suitable to requirements |  |
| 15.2 | Minimum protection class |  | IP55 |  |
| 15.3 | Minimum thickness of cabinet enclosure | mm | ≥2 |  |
| 15.4 | Limit switch contact of disconnector |  | ≥(2NO+2NC) |  |
| 15.5 | Auxiliary switch contact of disconnector |  | ≥(12NO+12NC) |  |
| 15.6 | Auxiliary switch contact of earthing switch |  | ≥(8NO+8NC) |  |
| 15.7 | Rated DC current of the auxiliary contact | A | 10 |  |
| 15.8 | DC current withstands short-time of the auxiliary contact |  | 100 A/30 ms |  |
| 15.9 | Selection switch of Local/Remote |  | yes |  |
| 15.10 | "Open/Close" push buttons of disconnector, earthing switch |  | yes |  |
| 15.11 | Motor and MCBs with auxiliary contacts have separate power supply |  | yes |  |
| 15.12 | Overcurrent and overload protection for the motor |  | yes |  |
| 15.13 | Drying system with temperature sensor, led lighting, drying and lighting have separate power supply by MCBs with auxiliary contacts |  | yes |  |
| 15.14 | Electrical interlock circuit between disconnector and earthing switch |  | yes |  |
| 16 | Supply voltage: |  |  |  |
| 16.1 | Motor | VDC | 220 (+10%; -15%) |  |
| 16.2 | Trip and Close | VDC | 220 (+10%; -15%) |  |
| 16.3 | Heating and Lighting | VAC | 220 (+10%; -15%) |  |
| 17 | Material of support structures for disconnector |  | Galvanized steel |  |
| 18 | HV terminals: |  |  |  |
| 18.1 | Materials |  | Aluminum alloy /copper |  |
| 18.2 | Dimensions |  | suitable for conductor |  |
| 18.3 | Bolt |  | Stainless steel |  |
| 19 | Catalogues |  | To be supplied |  |
| 20 | Requirements for testing (according to Technical Specification) |  | Yes The Bidder shall be filled list of test report as shown in item 2.21 |  |
| 21 | The remaining parameters or different will comply with the provisions of 1676/QĐ-EVNNPT date 24/08/2025 |  | Yes |  |

- 35 kV Disconnector and Earthing switch

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 62271-102 |  |
|  | Type |  | Outdoor, center-break, 3 poles, horizontal rotary |  |
|  | Disconnector drive |  |  |  |
| - | Main blade |  | Motor and Manual |  |
| - | Earthing blade |  | Motor and Manual |  |
|  | Nominal voltage | kV | 35 |  |
|  | Rated voltage | kV | 38,5 |  |
|  | Rated current | A | ≥630 |  |
|  | Frequency | Hz | 50 |  |
|  | Short time withstand current (1 sec.) | kArms. | ≥ 25 |  |
|  | Rated peak withstand current | kA peak | ≥ 62.5 |  |
|  | Rated duration of short-circuits | sec | ≥ 1 |  |
|  | Lighting impulse voltage (1.2/50µs) withstand of disconnector: |  |  |  |
| - | Line to earth | kV peak | >185 |  |
| - | Across open disconnector | kV peak | >185 |  |
|  | Power frequency withstand voltage |  |  |  |
| - | Phase - Earth | kV rms. | ≥ 80 |  |
| - | Across open disconnector | kV rms. | ≥ 80 |  |
|  | Resistance of main contact (new contact) | µΩ | To be specified |  |
|  | Support Insulator: |  |  |  |
| - | Applicable standard |  | IEC 60273 or equivalent |  |
| - | Type |  | To be specified |  |
| - | Material |  | Brown porcelain |  |
| - | Minimum nominal creepage distance | mm/kV | 31 |  |
| - | Minimum nominal specific creepage distance | mm | Comply with IEC 60815 |  |
| - | Maximum impact load when the disconnector is in operation, kN |  | To be specified |  |
|  | Air distance: - Between phase to earth - Between two poles in same phase (open condition) | mm | >400 |  |
|  | Operating voltage |  | (for engine-driven DS) |  |
|  | Drive motor | VDC | 220 (+10%; -15%) |  |
|  | Drying, lighting | VAC | 220 (+10%; -15%) |  |
|  | Controls switching of isolators and grounding switches, interlocking coils | VDC | 220 (+10%; -15%) |  |
|  | Operate to close/open ES, DS |  | Yes |  |
|  | Mechanical interlock mechanism between DS and ES |  | Yes |  |
|  | The opening/closing operation of the mobile phone does not use counterweights |  | Comply |  |
|  | Total weight | kg | To be specified |  |
|  | On-site control cabinets DCL, DTD |  |  |  |
|  | Code |  | To be specified |  |
|  | Design |  | To be specified |  |
|  | Country |  | To be specified |  |
|  | Minimum IP protection level |  | IP55 |  |
|  | Number of DCL travel contacts |  | ≥ (2NO+2NC) |  |
|  | DCL auxiliary contact number |  | ≥ (6NO+6NC) |  |
|  | Number of auxiliary contacts of the telephone (if the knife is controlled by motor) |  | ≥ (4NO+4NC) |  |
|  | Local and remote control lock |  | yes |  |
|  | Single button opens/closes DCL, DTD |  | yes |  |
| - | The motor and circuit breaker have separate power supply contacts for the motor circuit |  | yes |  |
|  | Equipped with overcurrent and overload protection for the motor |  | yes |  |
| - | The drying, lighting and circuit-breaker systems have separate power supply contacts for the drying and lighting circuits |  | yes |  |
|  | Electrical interconnects between DS and ESs |  | yes |  |
|  | Supporting structure |  |  |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Materials |  | Hot dip galvanized steel |  |
|  | HV connectors |  |  |  |
| - | Material |  | Aluminum/copper alloy |  |
| - | Dimensions |  | Suitable for conductors |  |
| - | Pole clamp bolt |  | Made of stainless steel |  |
| - | Technical documents included |  | Vietnamese /English |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes The Bidder shall be filled list of test report as shown in item 2.21 |  |
|  | The remaining parameters or different will comply with the provisions of 271/QĐ-EVN dated 24/07/2019 |  | Yes |  |

Other requirements of goods eligibility:

All Disconnector and Earthing switch (Designation HCB) from Siemens - India shall not be allowed for bid according to EVNNPT official document No. 3140/EVNNPT-KT + PC + ĐT + QLĐT+ QLXD, dated 11/09/2019).

- 500kv current transformer

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Model type |  | To be specified |  |
|  | Applicable standard |  | IEC 61869 |  |
|  | Type |  | Outdoor, single phase, top core, oil paper immersed |  |
|  | Rated voltage | kV | 550 |  |
|  | Frequency | Hz | 50 |  |
|  | Lightning impulse withstand voltage (1.2/50μs) | kV | ≥1550 |  |
|  | Switching impulse withstand voltage | kV | ≥1175 |  |
|  | Power frequency withstand voltage (01 minute) |  |  |  |
|  | - Primary windings | kV | ≥ 680 |  |
|  | - Secondary windings | kV | 03 |  |
|  | Housing insulator: |  |  |  |
|  | - Applicable standard |  | To be specified |  |
|  | - Material |  | Brown porcelain |  |
|  | - Minimum creepage distance | mm/ kV | 31 |  |
|  | - Total creepage distance | mm | ≥ 17050 |  |
|  | - Average diameter of insulator | mm | To be specified |  |
|  | - Minimum clearance between phase to earth | mm | Comply with IEC 60071-1 |  |
|  | Rated primary current | A | ≥4000 |  |
|  | Extended current rating |  | 120% of Rated |  |
|  | Rated transformation ratio |  | 1000-2000-3000-4000/1/1/1/1/1/1 |  |
|  | Rated thermal withstand current (1 sec.) | kA | 50 |  |
|  | Rated dynamic withstand current | kA | 125 |  |
|  | Maximum partial discharge level at 1.1Un (highest system voltage) | pC | To be specified |  |
|  | Number of secondary windings: |  | 06 |  |
|  | Core characteristics: Rated burden; accuracy class |  |  |  |
|  | Core No.1, 2 |  | 15VA – Cl. 0.5 |  |
|  | Core No. 3, 4, 5, 6 |  | 30VA – Cl. 5P20 |  |
|  | - All burdens, accuracy classes at all ratios |  | Yes |  |
|  | Limits of current error and phase displacement |  |  |  |
|  | - For secondary windings with class 0.5 (at 25%÷100% Rated Burden) |  | Comply with Table 201 (IEC 61869-2) |  |
|  | - For secondary windings with class 5P20 (at 25%÷100% Rated Burden) |  | Comply with Table 205 (IEC 61869-2) |  |
|  | Multi-Ratio shall be changed on secondary winding |  | Yes |  |
|  | Secondary winding resistance | Ω | To be specified |  |
|  | Knee-point voltage |  | To be specified |  |
|  | Temperature rise | oC | 65 |  |
|  | Terminal: |  |  |  |
|  | - Materials |  | To be specified |  |
|  | - Dimensions |  | To be specified |  |
|  | - Holes - No. , size and spacing |  | At least 6 holes |  |
|  | Total weight | kg | To be specified |  |
|  | Calculated wind load moment about base | kN | To be specified |  |
|  | Operating time of CT: |  |  |  |
|  | - Total operating time until maintain | Year | ≥ 10 |  |
|  | - Total operating time until replacement | Year | ≥ 20 |  |
|  | Approved by STAMEQ all CTs |  | As scope of supply |  |
|  | Supporting structure |  | As scope of supply |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Materials |  | hot dip galvanized steel |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes The Bidder shall be filled list of test report as shown in item 2.21 |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 1819/QĐ-EVNNPT date 16/09/2025 |  | Yes |  |

- 220kV Current Transformer

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 60044-1, 2 IEC 61869-1, 2 |  |
|  | Type |  | Outdoor, single phase, oil paper immersed, Top core, reinforce safety design |  |
|  | Rated voltage | kV | 245 |  |
|  | Frequency | Hz | 50 |  |
|  | Impulse Voltage (1.2/50µs) withstand | kV | ≥1050 |  |
|  | Power Frequency Voltage withstand |  |  |  |
| - | Primary windings | kV | ≥460 |  |
| - | Secondary windings | kV | 3 |  |
|  | Housing insulator: |  |  |  |
| - | Applicable standard |  | To be specified |  |
| - | Material |  | Brown porcelain |  |
| - | Minimum nominal creepage distance | mm/kV | ≥31 |  |
| - | Total Minimum nominal specific creepage distance | mm | ≥7595 |  |
| - | Average diameter of insulator |  | To be specified |  |
|  | Rated Primary Current |  |  |  |
| - | Type 1, 2 | A | 4000 |  |
| - | Type 3 | A | 3000 |  |
| - | Type 4 | A | 2000 |  |
|  | Phase to Earth Clearance | mm | ≥ 2100 |  |
|  | Extended Current Rating |  | 120% of Rated |  |
|  | Rated Transformation Ratios |  |  |  |
| - | Type 1 | A | 1200-2000-3000-4000/1/1/1/1/1 |  |
| - | Type 2 | A | 800-1200-2000-3000-4000/1/1/1/1/1 |  |
| - | Type 3 | A | 1200-2000-3000/1/1/1/1/1 |  |
| - | Type 4 | A | 800-1200-2000/1/1/1/1/1 |  |
|  | Rated Thermal Withstand Current (1 sec.) | kA | 50 |  |
|  | Rated Dynamic Withstand Current | kA | 125 |  |
|  | Operating time of CT |  |  |  |
| - | Total operating time until maintain | Year | ≥ 8 |  |
| - | Total operating time until replacement | Year | ≥ 20 |  |
|  | Maximum Partial Discharge Level at 1.1 Un (highest system voltage) | pC | To be specified |  |
|  | Secondary Winding Resistance | Ω | To be specified |  |
|  | Terminals |  |  |  |
| - | Materials |  | To be specified |  |
| - | Dimensions |  | To be specified |  |
| - | Number of hole (minimum 6 holes) |  | To be specified |  |
|  | Total Weight | kg | To be specified |  |
|  | Calculated Wind Load Moment about Base | kN | To be specified |  |
|  | Core Characteristics: Rated Burden, Accuracy Class (Type 1 & 2) |  |  |  |
| + | Core No. 2, 3 |  | 10VA - Cl 0.5 |  |
| + | Core No. 1, 4, 5 |  | 30VA - Cl 5P20 |  |
|  | All burdens, accuracy Classes at all ratios |  | Yes |  |
|  | Limits of current error and phase displacement |  |  |  |
| - | For secondary windings with class 0.5 (at 25%÷100% Rated Burden) |  | Comply with: Table 11 - IEC 60044-1 or Table 201-IEC 61869-1 |  |
| - | For secondary windings with class 5P20 (at 25%÷100% Rated Burden) |  | Comply with: Table 14 - IEC 60044-1 or Table 205-IEC 61869-1 |  |
|  | Multi-Ratio shall be changed on secondary winding |  | Yes |  |
|  | Approved by STAMEQ |  | As Scope of Supply |  |
|  | Temperature rise | 0C | 65 |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes The Bidder shall be filled list of test report as shown in item 2.21 |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 1819/QĐ-EVNNPT date 16/09/2025 |  | Yes |  |

- 35kV Current Transformer

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin/ Address |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Catalogue number |  | To be specified |  |
|  | Applicable standard |  | IEC 61869-1, IEC 61869-2 or TCVN 11845-2 or TCVN 7697-1 or equivalent |  |
|  | Type |  | Outdoor, single phase, oil immersed or solid insulation (Epoxy Resin) |  |
|  | Maximum Rated voltage | kV | 38,5 |  |
|  | Impulse Voltage (1.2/50µs) withstand | kVP | >180 |  |
|  | Power Frequency Voltage withstand |  |  |  |
|  | -Primary windings |  | >75 |  |
|  | -Secondary windings |  | >3 |  |
|  | Method of neutral grounding |  | Isolated |  |
|  | Frequency | Hz | 50 |  |
|  | Number of secondary windings |  |  |  |
|  | Type 1: 50-100/1/1A |  | 01 for protection 01 for measurement |  |
|  | Type 1: 1600-2000-2500/1/1A |  | 01 for protection 01 for measurement |  |
|  | Core Characteristics: Rated Burden, Accuracy Class |  |  |  |
|  | Core No. 1 |  | 30VA - Cl 5P20 |  |
|  | Core No. 2 |  | 10VA - Cl 0.5 |  |
|  | Rated current of primary windings (Ir1 1 – Ir1 2) |  |  |  |
|  | Type 1 | A | 50-100/1/1 |  |
|  | Type 2 | A | 1600-2000-2500/1/1 |  |
|  | Rated current of second windings (Ir2) | A | 1 |  |
|  | Continuously overload withstand current on primary | A | ≥ 1.2 x Ipr |  |
|  | Thermally stable current in 1 second | kA | ≥25 |  |
|  | Rated peak withstand current | kA peak | ≥ 2.5 x Ith |  |
|  | The partial discharge level shall not exceed the partial discharge test voltage limit 1,2Um/sqrt(3) |  |  |  |
|  | - Epoxy Resin | pC | 20 |  |
|  | - Oil immersed | pC | 05 |  |
|  | Temperature rise limit | oC | ≤ 60 |  |
|  | Minimum creepage distance | mm/ kV | ≥ 31 |  |
|  | Terminals |  |  |  |
| - | Materials |  | To be specified |  |
| - | Dimensions |  | To be specified |  |
| - | Number of hole (minimum 6 holes) |  | To be specified |  |
|  | Oil level indicator (for oil immersed) |  | Yes |  |
|  | Secondary terminal box design, seal hole |  | - Secondary terminal box made of aluminum, aluminum alloy, stainless steel or hot-dip galvanized steel. - The lid of the box or the base of the box and the bolts of the cover must have holes drilled for threading the sealing lead |  |
|  | Connector label |  | The connector label must allow identification of: - Primary and secondary coil - Coil segments (if any) - Relevant polarity of coils and coil sections - intermediate steps (if any) Terminals shall be clearly and conspicuously marked on the surface or in the vicinity of the connector. This labeling must include: - Letters after or before numbers. Letters must be capital letters. - The symbols of the current transformer terminals shall comply with the relevant TCVN or IEC standards |  |
|  | Device label |  | Current transformers must have a label permanently attached to the body with the following minimum contents: - Manufacturer's name or other mark which allows for easy identification of the manufacturer. - Code, serial number - Year of manufacture. - Rated primary and secondary currents. - Rated frequency. - Rated power and accuracy grade. - Maximum voltage of the device. - Rated insulation level. - Thermal stabilizing current (Ith) and dynamic stabilizing current (if different 2.5 times Ith) - Insulation class (if different from class A). All information is guaranteed not to fade over the operating life. |  |
|  | Accessory |  | - Medium voltage terminals and clamps must be made of tin-plated or nickel-plated copper to connect copper/aluminum wires with cross-sections in accordance with design requirements. - The parts and bolts must be made of hot-dip galvanized steel or stainless steel. |  |
|  | Type test |  | Yes The Bidder shall be filled list of test report as shown in item 2.21 |  |
|  | The remaining parameters or different will comply with the provisions of 105/QĐ-HĐTV date 21/09/2021 of EVN |  | Yes |  |

- 500kV Capacitor Voltage Transformer

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Catalogue number |  | To be specified |  |
|  | Applicable standard |  | IEC 61869-5 |  |
|  | Type |  | Outdoor, single phase, oil immersed |  |
|  | Rated voltage | kV | 550 |  |
|  | Frequency | Hz | 50 |  |
|  | Lightning impulse withstand voltage (1.2/50μs) | kV | ≥1550 |  |
|  | Switching impulse withstand voltage | kV | ≥1175 |  |
|  | Power frequency withstand voltage (01 minute) |  |  |  |
|  | - Primary winding | kV | ≥680 |  |
|  | - Secondary winding | kV | ≥3 |  |
|  | Guaranteed limits of rated capacitance | % | To be specified |  |
|  | Rated maximum HF current | A | To be specified |  |
|  | Temperature co-efficient of capacitance per 0C |  | To be specified |  |
|  | Maximum partial/discharge level .pC | kV | To be specified |  |
|  | Housing insulator: |  |  |  |
|  | - Applicable standard |  | To be specified |  |
|  | - Material |  | Brown porcelain |  |
|  | - Minimum creepage distance | mm/ kV | ≥31 |  |
|  | - Total creepage distance | mm | ≥17050 |  |
|  | - Average diameter of insulator | mm | To be specified |  |
|  | - Minimum clearance between phase to earth | mm | Comply with IEC 60071-1 |  |
|  | Rated mechanical terminal load | kN | 02 |  |
|  | Facilities for fitting of line trap |  | If any |  |
|  | Maximum permissible top wind loading | km/hr | To be specified |  |
|  | Calculated wind load moment about base | kN | To be specified |  |
|  | Flux density at rated voltage | Tesla | To be specified |  |
|  | Recommended fuse ratings |  |  |  |
|  | Weight of intermediate voltage transformer | kg | To be specified |  |
|  | Oil outlet and oil test valve | Yes | To be specified |  |
|  | Voltage ratio, burden, accuracy class |  |  |  |
|  | - Winding No.1 |  | 500kV:√3/110V:√3 25VA – Cl. 0.5 |  |
|  | - Winding No.2 |  | 500kV:√3/110V:√3 50VA – Cl. 3P |  |
|  | Over-voltage capability |  |  |  |
|  | - Continuous |  | 1.2 Ur |  |
|  | - 30 sec. |  | 1.5 Ur |  |
|  | Temperature rise | 0C | ≤65 |  |
|  | HV terminals: |  | To be specified |  |
|  | - Material |  |  |  |
|  | - Dimensions |  |  |  |
|  | - Holes - No. , size and spacing |  | At least 6 holes |  |
|  | Weight of capacitor voltage transformer | kg | To be specified |  |
|  | Approved by STAMEQ for all CVTs |  | As Sope of Supply |  |
|  | Operating time of CVT: |  |  |  |
|  | - Total operating time until maintain | Year | ≥ 10 |  |
|  | - Total operating time until replacement | Year | ≥ 20 |  |
|  | Supporting structure |  | As Scope of Supply |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Materials |  | hot dip galvanized steel |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes The Bidder shall be filled list of test report as shown in item 2.21 |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 1816/QĐ-EVNNPT date 16/09/2025 |  | Yes |  |

220kV Capacitor Voltage Transformer

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 60044-2, IEC 60044-5, IEC 61869-5, IEC 60815, IEC 60071, IEC 60137 (2008), IEC 60358-3 (2013) |  |
|  | Type |  | Outdoor, single phase, oil paper immersed, |  |
|  | Rated voltage | kV | 245 |  |
|  | Frequency | Hz | 50 |  |
|  | Impulse Voltage (1.2/50µs) Withstand | kV peak | ≥1050 |  |
|  | Power Frequency Voltage Withstand |  |  |  |
| - | Primary windings | kV rms. | ≥460 |  |
| - | Secondary windings | kV | ≥3 |  |
|  | Rated Maximum HF Current | A | To be specified |  |
|  | Temperature Co-efficient of capacitance per oC |  | To be specified |  |
|  | Maximum Partial/Discharge Level .pC | kV | To be specified |  |
|  | Housing insulator: |  |  |  |
| - | Applicable standard |  | To be specified |  |
| - | Material |  | Brown porcelain |  |
| - | Minimum nominal creepage distance | mm/kV | ≥31 |  |
| - | Minimum nominal specific creepage distance | mm | ≥7595 |  |
| - | Average diameter of insulator | mm | To be specified |  |
|  | Phase to Earth Clearance | mm | ≥ 2100 |  |
|  | Rated Mechanical Terminal Load | kN | To be specified |  |
|  | Facilities for fitting of line trap |  | If any |  |
|  | Max. Permissible Top Wind Loading | km/hr | To be specified |  |
|  | Calculated Wind Load Moment about Base | kNm | To be specified |  |
|  | HV Terminals |  | To be specified |  |
| - | Material |  |  |  |
| - | Dimensions |  |  |  |
| - | Number of hole (minimum 6 holes) or stud type |  | To be specified |  |
|  | Weight of capacitor voltage transformer | kg | To be specified |  |
|  | Flux Density at Rated Voltage | Tesla | To be specified |  |
|  | Recommended Fuse Ratings |  | To be specified |  |
|  | Weight of Intermediate Voltage Transformer | kg | To be specified |  |
|  | Oil outlet and oil test valve |  | Yes |  |
|  | Voltage ratio, burden, accuracy class |  |  |  |
| - | Winding No.1 |  | 220kV:√3 /110V:√3 25VA - Cl 0.5 |  |
| - | Winding No.2 |  | 220kV:√3 /110V:√3 50VA - 3P |  |
|  | Maximum simultaneous burden output/ accuracy class |  | 25VA for class 0.5 50VA for class 3P |  |
|  | Limits of voltage error and phase displacement |  |  |  |
| - | For secondary windings with class 0.5 (at 25%÷100% Rated Burden) |  | Comply with: Table 11 - IEC 60044-2 or Table 501-IEC 61869-5 |  |
| - | For secondary windings with class 5P20 (at 25%÷100% Rated Burden) |  | Comply with: Table 12 - IEC 60044-2 or Table 502-IEC 61869-5 |  |
|  | Approved by STAMEQ for all CVTs |  | As Scope of Supply |  |
|  | Over volt capability |  |  |  |
| - | Continuous |  | 1.2x220kV/√3 |  |
| - | 30 sec |  | 1.5x220kV/√3 |  |
|  | Temperature rise | 0C | 65 |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes The Bidder shall be filled list of test report as shown in item 2.21 |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 1816/QĐ-EVNNPT date 16/09/2025 |  | Yes |  |

35kV Inductive Voltage Transformer

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacture/ Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 61869-1, -3 or TCVN 11845-3 or TCVN 7697-2 or equivalent |  |
|  | Type |  | Outdoor, inductive voltage transformer, single phase, oil immersed or epoxy resin |  |
|  | Maximum Rated voltage | kV | 38,5 |  |
|  | Rated voltage on primary winding | kV | 35/√3 |  |
|  | Rated voltage on Secondary winding | V | 110/√3 |  |
|  | Neutral point operating |  | Isolated |  |
|  | Frequency | Hz | 50 |  |
|  | Voltage ratio, burden, accuracy class |  |  |  |
| - | Winding No.1 |  | 35:√3 /0.11:√3 kV 25VA - Cl 0.5 |  |
| - | Winding No.2 |  | 35:√3 /0.11:√3 kV 25VA - Cl 3P |  |
| - | Winding No.3 |  | 35:√3 /0.11:3 kV 25VA - Cl 6P |  |
|  | Impulse Voltage (1.2/50µs) Withstand | kV peak | ≥180 |  |
|  | Power Frequency Voltage Withstand on Primary windings | kV rms. | ≥75 |  |
|  | Power Frequency Voltage Withstand on Secondary windings | kV | ≥3 |  |
|  | Over volt capability |  |  |  |
| - | Continuous |  | 1.2 |  |
| - | 30s |  | 1.9 applicable to power systems with neutral grounded through impedance |  |
|  | 8h |  | 1.9 applicable to isolated neutral power systems |  |
|  | Partial discharge level: limit shall not be exceeded at the partial discharge test voltage 1.2xUm/√3 |  |  |  |
|  | - Solid insulation | pC | 20 |  |
|  | - Immersion in liquid | pC | 05 |  |
|  | Temperature rise | oC | 60 |  |
|  | Minimum nominal creepage distance | mm/kV | ≥31 |  |
|  | Oil outlet and oil test valve (applicable to voltage transformers immersed in oil) |  | Yes |  |
|  | Second terminal box cover design, lead hole |  | - The secondary terminal cover is made of aluminum, aluminum alloy, stainless steel or hot-dip galvanized sheet steel. - The lid of the box or the base of the box and the bolts of the lid must have holes drilled to thread the sealing lead. |  |
|  | Connector label |  | The connector label shall allow identification of: - Primary and secondary coils. - Parts of the coil (if any). - The relevant poles of the coil and the coil. - Intermediate steps (if any). Terminals shall be clearly and conspicuously marked on the surface or vicinity of the connector. This labeling must include: - The letters are placed after or before the numbers. The letters must be capital letters. - Symbols of voltage transformer terminals shall be in accordance with relevant TCVN or IEC standards |  |
|  | Label for device |  | Votage transformers must have a label permanently attached to the body with the following minimum contents: - Manufacturer's name or other mark which allows for easy identification of the manufacturer. - Code, Serial number. - Year of manufacture. - Rated primary and secondary Voltage. - Rated frequency. - Rated power and accuracy grade. - Maximum voltage of the device. - Rated insulation level - Overvoltage factor over time. - Insulation class (if different from class A). All information is guaranteed not to fade over operating life |  |
|  | Approved by STAMEQ for all VTs |  | As Sope of Supply |  |
|  | HV Terminals |  | To be specified |  |
|  | Material |  | To be specified |  |
|  | Dimensions |  | To be specified |  |
|  | Number of hole |  | To be specified |  |
|  | Weight of capacitor voltage transformer | kg | To be specified |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes The Bidder shall be filled list of test report as shown in item 2.21 |  |
|  | Catalogues |  | To be specified |  |
|  | The remaining parameters or different will comply with the provisions of 104/QĐ-HĐTV date 21/09/2021 of EVN |  | Yes |  |

500kv surge arrester

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Model type |  | To be specified |  |
|  | Applicable standard |  | IEC 60099-4 |  |
|  | Rated frequency | Hz | 50 |  |
|  | System voltage | kV | 500 |  |
|  | Maximum voltage | kV | 550 |  |
|  | Neutral earthing |  | Direct |  |
|  | Type |  | Outdoor |  |
|  | Allowable overvoltage factor under single-phase earth fault |  | 1.4 |  |
|  | Surge arrester connection arrangement |  | Phase-to-Earth |  |
|  | Technical parameters |  |  |  |
|  | Type |  | Outdoor, ZnO, gapless |  |
|  | Rated voltage | kV | ≥420 |  |
|  | Maximum continuous operating voltage (Uc) | kV | ≥333 |  |
|  | Temporary overvoltage TOV | kVrms | To be specified |  |
|  | Nominal discharge current | kA | ≥20 |  |
|  | Peak discharge current | kAp | ≤100 |  |
|  | energy absorption capability | kJ/kV Ur | ≥10 |  |
|  | Repetition discharge capability – Qrs, | C | ≥2.4 |  |
|  | Voltage grading ring | mm | Yes |  |
|  | Arrester housing: |  |  |  |
|  | Material |  | Porcelain |  |
|  | Rated short-duration power-frequency withstand voltage | kV | ≥620 |  |
|  | Rated switching impulse withstand voltage | kV peak | ≥1175 |  |
|  | Rated lightning impulse withstand voltage (1,2/50 µs-BIL), | kV peak | ≥1550 |  |
|  | Minimum nominal creepage distance | mm/kV | ≥31 |  |
|  | Rated short cicuit curent | kA | ≥50 |  |
|  | specified long term load | N | ≥600 |  |
|  | specified short term load | N | ≥1500 |  |
|  | Mean breaking load | N | ≥1800 |  |
|  | Lightning counter with leakage current display |  | Yes |  |
|  | Manufacture/ Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Number of digits of lightning counter |  | ≥ 5 |  |
|  | Leakage current measurement range |  | To be specified |  |
|  | Sensitivity of lightning impulse | A | ≤ 200 |  |
|  | Impulse withstand capacity power (4/10 μs) | kA | ≥ 100 |  |
|  | protection degree |  | IP54 |  |
|  | Current leakage meter is capable of transmitting signal to the control room of the substation equipped with surge arrester for online monitoring of current leakage |  | Yes |  |
|  | Terminal materials |  | To be specified |  |
|  | Material |  | To be specified |  |
|  | Dimensions |  | To be specified |  |
|  | Terminal clamping bolt |  | Stainless steel or hot-dip galvanized steel |  |
|  | Number of hole (minimum 6 holes) |  | yes |  |
|  | Catalogues |  | To be supplied |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes The Bidder shall be filled list of test report as shown in item 2.21 |  |
|  | The remaining parameters or different will comply with the provisions of 1158/QĐ-EVNNPT of EVNNPT date 26/6/2025 and 2416/QĐ-EVNNPT of EVNNPT date 9/12/2025 |  | Yes |  |

220kV SURGE ARRESTER

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Model type |  | To be specified |  |
|  | Applicable standard |  | IEC 60099-4 |  |
|  | Rated frequency | Hz | 50 |  |
|  | System voltage | kV | 220 |  |
|  | Maximum voltage | kV | 245 |  |
|  | Neutral earthing |  | Direct |  |
|  | Type |  | Outdoor |  |
|  | Allowable overvoltage factor under single-phase earth fault |  | 1.4 |  |
|  | Surge arrester connection arrangement |  | Phase-to-Earth |  |
|  | Technical parameters |  |  |  |
|  | Type |  | Outdoor, ZnO, gapless |  |
|  | Rated voltage Ur | kV | ≥192 |  |
|  | Maximum continuous operating voltage (Uc) | kV | ≥152 |  |
|  | Temporary overvoltage TOV | kVrms | To be specified |  |
|  | Nominal discharge current | kA | ≥10 |  |
|  | Peak discharge current | kAp | ≤100 |  |
|  | energy absorption capability | kJ/kV Ur | ≥7 |  |
|  | Repetition discharge capability – Qrs, | C | ≥1,6 |  |
|  | Voltage grading ring | mm | To be specified |  |
|  | Arrester housing: |  |  |  |
|  | Material |  | Porcelain or Polymer |  |
|  | Rated short-duration power-frequency withstand voltage | kV | ≥460 |  |
|  | Rated lightning impulse withstand voltage (1,2/50 µs-BIL), | kV peak | ≥1050 |  |
|  | Minimum nominal creepage distance | mm/kV | ≥31 |  |
|  | Rated short cicuit curent | kA | ≥50 |  |
|  | specified long term load | N | ≥400 |  |
|  | specified short term load | N | ≥1000 |  |
|  | Mean breaking load | N | ≥1200 |  |
|  | Lightning counter with leakage current display |  | Yes |  |
|  | Manufacture/ Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Number of digits of lightning counter |  | ≥ 5 |  |
|  | Leakage current measurement range | mA | To be specified |  |
|  | Sensitivity of lightning impulse | A | ≤ 200 |  |
|  | Impulse withstand capacity power (4/10 μs) | kA | ≥ 100 |  |
|  | protection degree |  | IP54 |  |
|  | Current leakage meter is capable of transmitting signal to the control room of the substation equipped with surge arrester for online monitoring of current leakage |  | Yes |  |
|  | Terminal materials |  | To be specified |  |
|  | Material |  | To be specified |  |
|  | Dimensions |  | To be specified |  |
|  | Terminal clamping bolt |  | Stainless steel or hot-dip galvanized steel |  |
|  | Number of hole (minimum 6 holes) |  | yes |  |
|  | Catalogues |  | To be supplied |  |
|  | Requirements for testing (according to Technical Specification) |  | Yes The Bidder shall be filled list of test report as shown in item 2.21 |  |
|  | The remaining parameters or different will comply with the provisions of 1158/QĐ-EVNNPT of EVNNPT date 26/6/2025 and 2416/QĐ-EVNNPT of EVNNPT date 9/12/2025 |  | Yes |  |

35kV Surge Arrester

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
| I | General information of the manufacturer |  |  |  |
|  | Manufacture/ Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 60099-4 |  |
| II | Power system operating conditions |  |  |  |
|  | Maximum operating voltage of the electrical system | kV | 38,5 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Operating mode of the system |  | Neutral isolated from the ground |  |
|  | Allowable overvoltage factor in single-phase earth fault |  | ≥ 1.73 |  |
|  | Maximum duration of temporary overvoltage | s | 7200 |  |
|  | Surge arrester connection arrangement |  | Phase-to-Earth |  |
| III | Technical specifications of the surge arrester |  |  |  |
|  | Type |  | Outdoor, ZnO, gapless, according to IEC |  |
|  | Level of SA |  | DH or class 1 |  |
|  | Rated voltage (Ur) | kV | ≥ 48 |  |
|  | Maximum continuous operating voltage (UC) | kV | ≥ 38 |  |
|  | Temporarily overvoltage voltage with TOV characteristic curve | kVrms | To be specified |  |
|  | Nominal discharge current | kA | ≥ 10 |  |
|  | Peak discharge current | kApeak | ≥ 100 |  |
|  | Insulation coordination coefficient |  | ≥ 1.3 |  |
| IV | Arrester housing: |  |  |  |
|  | Material |  | Porcelain or Silicon rubler (SR) |  |
|  | Lightning impulse withstand (1,2/50μs) | kVpeak | ≥ 180 |  |
|  | Power frequency withstand voltage of the insulation (50Hz/1 min) | kVrms | ≥ 75 |  |
|  | Minimum nominal creepage distance | mm/kV | ≥ 31 |  |
|  | Static load capacity | kN | To be specified |  |
|  | Dynamic load capacity | kN | To be specified |  |
| V | Other accessories |  |  |  |
|  | Lightning counter with leakage current display |  | To be specified |  |
| - | Manufacture/ Country of Origin |  | To be specified |  |
| - | Place of factory |  | To be specified |  |
| - | Designation |  | To be specified |  |
| - | Leakage current measurement range: 0-30mA |  | Yes |  |
| - | Number of digits of lightning counter |  | ≥ 5 |  |
| - | Sensitivity of lightning impulse |  | ≤ 200 |  |
| - | Impulse withstand capacity power (4/10 μs) | kA | ≥ 100 |  |
| - | IP 54 |  | yes |  |
|  | Terminal materials |  | To be specified |  |
| - | Material |  | To be specified |  |
| - | Dimensions |  | To be specified |  |
| - | Number of hole (minimum 6 holes) |  | yes |  |
|  | Type test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.21 |  |
|  | Technical document |  | English/Vietnamese |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 110/QĐ-HĐTV of EVN |  | Yes |  |

35kV Current limiting reactor

| No | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacture/Country of Origin |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Type |  | Out door, Air-core dry type, single phase |  |
|  | Applicable standard |  | IEC 60076-6 / IEEE C57.16 |  |
|  | Rated voltage | kV | 38,5 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Rated current | A | 50 |  |
|  | Impulse Voltage Withstand (BIL), | kV peak | 180 |  |
|  | Power frequency withstand voltage, | kV rms | 75 |  |
|  | Short circuit current withstand |  |  |  |
|  | Thermal Short Circuit Current | kA | 10 |  |
|  | Mechanical Short Circuit Current withstand | kA | 25 |  |
|  | Thermal short-circuit withstand duration, | s | 2 |  |
|  | Impedance per phase | Ω | To be specified |  |
|  | Reactance per phase | Ω | To be specified |  |
|  | Inductance | mH | 1,5mH |  |
|  | Total losses per phase /at nominal capacity: | kW | To be specified |  |
|  | Installation |  | Outdoor |  |
|  | Insulating medium |  | air |  |
|  | Type of cooling |  | Natural air |  |
|  | Thermal class | Class | F |  |
|  | Guaranteed value of sound level for unit(2m from coil surface) | dB | 75 |  |
|  | Dimensions | mm | To be specified |  |
|  | Weight | kg | To be specified |  |
|  | Paint Color |  | ANSI 70 / gray |  |
|  | ISO Quality Management System Certificate |  | 9001, 14001 |  |
|  | BASE INSULATOR |  |  |  |
| 22.1 | Manufacture/Country of Origin |  | To be specified |  |
| 22.2 | Applied Standard |  | EC 60273/IEC 60815 or equivalent |  |
| 22.3 | Material |  | Porcelain |  |
| 22.4 | Type |  | Station post insulator, outdoor |  |
| 22.5 | Minimum nominal creepage distance | mm/kV | ≥31 |  |
| 22.6 | Minimum failing load IEC60168 |  |  |  |
|  | - Bending |  | To be specified |  |
|  | - Torsion |  | To be specified |  |
| 25 | SUPPORT STRUCTURE |  | Yes |  |
| 25.1 | Manufacture/Country of Origin |  | To be specified |  |
| 25.2 | Material |  | Hot dip galvanized steel |  |
| 26 | Type test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.21 |  |

500kV Post Insulator

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Model type |  | To be specified |  |
|  | Applicable standard |  | IEC 60273 |  |
|  | Insulator material |  | Porcelain |  |
|  | Type |  | C10-1550 |  |
|  | Dimensions (State Tolerances.): |  |  |  |
|  | - Height | mm | To be specified |  |
|  | - Average diameter of insulator | mm | To be specified |  |
|  | Minimum nominal creepage distance | mm/kV | ≥ 31 |  |
|  | Minimum nominal specific creepage distance | mm | ≥ 17050 |  |
|  | Phase to Earth Clearance | mm | Comply with IEC 60071-1 |  |
|  | Mechanical |  |  |  |
|  | - Minimum Failing Load-bending | kN | 10 |  |
|  | - Minimum Failing Moment-torsion | kNm | 4 |  |
|  | Electrical |  |  |  |
|  | Power Frequency Withstand Voltage | kV | 680 |  |
|  | Light Impulse Voltage (1.2/50µs) Withstand | kV peak | 1550 |  |
|  | Fixing Arrangements |  | To be specified |  |
|  | - Top Cap PCD | mm |  |  |
|  | - Top Cap Fixing Holes - number x size | mm | At least 6 holes |  |
|  | - Base PCD |  |  |  |
|  | - Base Fixing Holes - number x size |  | At least 6 holes |  |
|  | Weight of complete Post Insulator | kg | To be specified |  |
|  | Requirements for testing (according to Technical Specification) |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.21 |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 0103/QĐ-EVNNPT date 11/7/2019. |  | Yes |  |

220kV Post Insulator

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 60273 |  |
|  | Rated voltage | kV | ≥245 |  |
|  | Insulator material |  | Porcelain |  |
|  | Type |  | To be specified |  |
|  | Dimensions (State Tolerances.): |  |  |  |
| - | Height | mm | To be specified |  |
| - | Average diameter of insulator | mm | To be specified |  |
|  | Minimum nominal creepage distance | mm/kV | ≥31 |  |
|  | Total Minimum nominal specific creepage distance | mm | ≥ 7595 |  |
|  | Phase to Earth Clearance | mm | ≥ 2100 |  |
|  | Minimum insulation puncture voltage | kV | ≥ 1050 |  |
|  | Mechanical |  |  |  |
| - | Minimum Failing Load-bending | kN | 8 |  |
| - | Minimum Failing Moment-torsion | kNm | 4 |  |
|  | Electrical |  |  |  |
|  | a. Power Frequency Withstand Voltage | kV | 460 |  |
|  | b. Light Impulse Voltage (1.2/50µs) Withstand | kV peak | 1050 |  |
|  | Fixing Arrangements |  | To be specified |  |
| - | Top Cap PCD | mm |  |  |
| - | Top Cap Fixing Holes - number x size | mm |  |  |
| - | Base PCD |  |  |  |
| - | Base Fixing Holes - number x size |  | At least 6 holes |  |
|  | Weight of complete Post Insulator | kg | To be specified |  |
|  | Requirements for testing (according to Technical Specification) |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.21 |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 0103/QĐ-EVNNPT date 11/7/2019. |  | Yes |  |

500kV SUSPENSION AND TENSION INSULATOR

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Insulator unit |  |  |  |
|  | Manufacturer/ Country of Origin of insulator and Fitting of insulator string |  | To be specified |  |
|  | Catalogue number |  | To be specified |  |
|  | Insulating material |  | Toughened glass or porcelain |  |
|  | Applicable standard |  | IEC 60305; IEC-60120 |  |
|  | Type of insulator unit |  | 160BLP |  |
|  | Fixing type to Gantry beam |  | U-bolt |  |
|  | Shed diameter | mm | To be specified |  |
|  | Unit spacing | mm | 170 |  |
|  | Minimum creeepage distance | mm | ≥ 525 |  |
|  | Wet power frequency withstand voltage - min. |  | 55 |  |
|  | Dry power frequency withstand voltage-min. |  | 90 |  |
|  | Lightning impulse withstand |  | 140 |  |
|  | Minimum puncture voltage in oil | kV | 130 |  |
|  | Zinc sleeve |  | Yes |  |
|  | Insulator set complete |  |  |  |
|  | Number of insulator strings in parallel per phase |  | 2 |  |
|  | Minimum eletcro-mechanical failing load complete set | kN | 2x160 |  |
|  | Total creeepage distance | mm | ≥ 17050 |  |
|  | Number of insulator disks in each string | disk | 2x36 |  |
|  | Overall length of set including clamp and all fittings |  | To be specified |  |
|  | - max | mm |  |  |
|  | - min | mm |  |  |
|  | Weight of complete set with all fittings | kg | To be specified |  |
|  | Turnbuckle for 500kV tension insulator |  | Yes |  |
|  | Arcing horn for 500kV insulator |  | Yes |  |
|  | Fittings |  |  |  |
|  | - Type of fittings |  | To be specified |  |
|  | - Dimension of U bolted | mm | To be specified |  |
|  | 50Hz flashover and withstand tests (complete sets) |  | To be specified |  |
|  | Dry flash over | kV |  |  |
|  | One minute wet withstand | kV |  |  |
|  | 50 percent impulse flashover |  | To be specified |  |
|  | 1.2/50µs negative wave | kV |  |  |
|  | 1.2/50µs positive wave | kV |  |  |
|  | Corona test voltage | kV | To be specified |  |
|  | Radio influence voltage measured at 1.1 times Us/√3 at 1MHz | µV | To be specified |  |
|  | Requirements for testing (according to Technical Specification) |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.21 |  |
|  | The remaining parameters or different will comply with the provisions of 1769/QĐ-EVNNPT date 09/09/2025 |  | Yes |  |

220kV Suspension and Tension Insulator

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Insulator unit |  |  |  |
| 1 | Manufacturer/Country of Origin of insulator and Fitting of insulator string |  | To be specified |  |
| 2 | Model type |  | U160BLP |  |
| 3 | Insulating material |  | Glass or ceramic |  |
| 4 | Applicable standard |  | IEC 60305; IEC-60120 |  |
| 5 | Type of coupling |  | Ball & socket |  |
| 6 | Size of coupling | mm | To be specified |  |
| 7 | Locking device |  | Split pin type |  |
| 8 | Minimum electro-mechanical failing load | kN | ≥ 160 |  |
| 9 | Shed diameter (mm) | mm | To be specified |  |
| 10 | Unit nominal spacing | mm | 170 |  |
| 11 | Creepage distance - min | mm | ≥ 525 |  |
| 12 | Total creepage distance | mm | ≥ 7502 |  |
| 13 | Dry power frequency withstand voltage - min. | kV | 90 |  |
| 14 | Wet power frequency withstand voltage-min. | kV | 55 |  |
| 15 | Lightning impulse withstand | kV | 140 |  |
| 16 | Minimum puncture voltage in oil | kV | 130 |  |
| 17 | Zinc sleeve |  | Yes |  |
|  | Insulator set complete |  |  |  |
| 18 | Number of insulator strings in parallel per phase |  | 1 |  |
| 19 | Min. electro - mechanical failing load complete set | kN | 1 x 160 |  |
| 20 | Number of insulator disk in each string | disk | 17 |  |
| 21 | Overall length of set including clamp and all fittings |  |  |  |
|  | max | mm | To be specified |  |
|  | min | mm | To be specified |  |
| 22 | Weight of complete set with all fittings | kg | To be specified |  |
| 23 | Turnbuckle for 220kV tension insulator |  | yes |  |
| 24 | Arcing horn for 220kV insulator |  | yes |  |
| 25 | Fittings |  |  |  |
|  | - Type of fittings |  | To be specified |  |
| 26 | Requirements for testing (according to Technical Specification) |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.21 |  |
| 27 | Catalogues |  | To be supplied |  |
| 28 | The remaining parameters or different will comply with the provisions of 1769/QĐ-EVNNPT date 09/09/2025 |  | Yes |  |

MALLEABLE ALUMINIUM ALLOY TUBE (E-Al MgSi 0.5F22)

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacturer/ Place of Manufacture | To be specified |  |
| 2 | Manufacture’s code | To be specified |  |
| 3 | Standard | ASTM-B317, EN 755-2 |  |
| 4 | Type | E-Al MgSi 0.5F22 |  |
|  |  | Ф160/144 |  |
| 5 | Outside diameter | 160mm |  |
| 6 | Inner diameter | 144mm |  |
| 7 | Tube's thickness | 8 |  |
| 8 | Cross-section | To be specified |  |
| 9 | Weight | To be specified |  |
| 11 | Continuous current capacity at max. operating temperature of 850C and in air of 350C | ≥4615A |  |
| 12 | Short time withstand current | 50 kA/1s |  |
| 13 | Electric DC. Resistance (at 20oC) | ≤ 0.01Ω/km |  |
| 14 | Elongation at fracture A5 min. | 8% |  |
| 15 | Minimum breaking load | >=170N/mm2 |  |
| 16 | Electrical conductivity a 200C | ≤ 30 m/Ωmm2 |  |
| 17 | Requirements for testing (according to Technical Specification) | To be supplied. The Bidder shall be filled list of test report as shown in item 2.21 |  |

All Aluminium Conductor (AAC-1000; AAC-800; AAC-630)

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Standard |  | IEC 61089 |  |
|  | Type 1 |  | AAC-1000 |  |
|  | Type 2 |  | AAC-800 |  |
|  | Type 3 |  | AAC-630 |  |
|  | Nominal cross section area: |  |  |  |
|  | Type 1 | mm2 | 1000 |  |
|  | Type 2 | mm2 | 800 |  |
|  | Type 3 | mm2 | 630 |  |
|  | Stranded number and diameter of strands |  | To be specified |  |
|  | Type 1 | mm | To be specified |  |
|  | Type 2 | mm | To be specified |  |
|  | Type 3 | mm | To be specified |  |
|  | Stranding direction of outer most layer |  | To be specified |  |
|  | Type 1 |  | To be specified |  |
|  | Type 2 |  | To be specified |  |
|  | Type 3 |  | To be specified |  |
|  | Minimum strength load |  | To be specified |  |
|  | Type 1 | kN | ≥160 |  |
|  | Type 2 | kN | ≥128 |  |
|  | Type 3 | kN | ≥100.8 |  |
|  | Modulus of elasticity of conductor |  |  |  |
|  | Type 1 | daN/mm2 | To be specified |  |
|  | Type 2 | daN/mm2 | To be specified |  |
|  | Type 3 | daN/mm2 | To be specified |  |
|  | Maximum mass of conductor |  |  |  |
|  | Type 1 | kg/km | To be specified |  |
|  | Type 2 | kg/km | To be specified |  |
|  | Type 3 | kg/km | To be specified |  |
|  | Requirements for testing |  | Yes |  |
|  | Continuous current capacity at max. operating temperature of 900C and in air of 250C |  |  |  |
|  | Type 1 | A | To be specified |  |
|  | Type 2 | A | To be specified |  |
|  | Type 3 | A | To be specified |  |
|  | Overall diameter of stranded conductor |  |  |  |
|  | Type 1 | mm | To be specified |  |
|  | Type 2 | mm | To be specified |  |
|  | Type 3 | mm | To be specified |  |
|  | Modulus of elasticity of conductor |  |  |  |
|  | Type 1 | daN/mm2 | To be specified |  |
|  | Type 2 | daN/mm2 | To be specified |  |
|  | Type 3 | daN/mm2 | To be specified |  |
|  | Maximum electric DC. resistance at 20oC |  |  |  |
|  | Type 1 | Ω/km | 0,0289 |  |
|  | Type 2 | Ω/km | 0,0289 |  |
|  | Type 3 | Ω/km | 0,0458 |  |
|  | Requirements for testing (according to Technical Specification) |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.23 |  |

Lightning wires (Phlox 94.1)

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Standard |  | AFNL C34-125, C34-112, C34-113, IEC-61089, TCVN 6483:1999 hoặc tương đương |  |
|  | Type |  | Phlox 94.1 |  |
|  | Material of lightning wire |  | Galvanized Steel |  |
|  | Construction (Aluminum alloy – steel core) | Number of wires/ Wire diameter (mm) | 15/2.1 + 19/1.68 |  |
|  | Total conductor cross-section area | mm2 | 94.1 |  |
|  | Aluminum alloy cross-section area | mm2 | 51.95 |  |
|  | Steel core cross-section area | mm2 | 42.12 |  |
|  | Overall diameter of conductor (*) | mm | 12.8 |  |
|  | Steel core diameter (**) | mm |  |  |
|  | Conductor weight (**) | kg/km |  |  |
|  | Conductor weight (without grease) (**) | kg/km |  |  |
|  | Weight of grease (**) | kg/km |  |  |
|  | Coefficient of linear thermal expansion (**) | 1/°C |  |  |
|  | Minimum rated tensile strength (IEC 61089) | daN | To be specified |  |
|  | Modulus of elasticity of conductor | daN/mm2 | To be specified |  |
|  | Maximum DC resistance at 20°C | Ω/km | 0.642 |  |
|  | Greasing |  | As per IEC 61089, TCVN 6483:1999 or equivalent |  |
|  | Minimum grease dropping point temperature | °C | 120 |  |
|  | Requirements for testing (according to Technical Specification) |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.21 |  |

Notes:
(*) Approximate values with tolerance as specified.
(**) Values provided by the Manufacturer.

35kV – ACSR-XLPE – 300/39mm2

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/ Country of Origin |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Standard |  | TCVN 5935-2/ IEC 60502-2; IEC 61089 |  |
|  | Type |  | 35kV – ACSR/XLPE/PVC |  |
|  | Nominal cross section area |  |  |  |
|  | - Aluminum | mm2 | 300 |  |
|  | - Steel | mm2 | 39 |  |
|  | Stranded number and diameter of strands: |  |  |  |
|  | - Aluminum | mm | 24/4.0 |  |
|  | - Steel | mm | 7/2.65 |  |
|  | Insulation |  | XLPE |  |
|  | - Thickness of insulation | mm | ≥5.5 |  |
|  | Stranding direction of outer most layer |  | To be specified |  |
|  | Minimum strength load | kN | To be specified |  |
|  | Modulus of elasticity of conductor | daN/mm2 | To be specified |  |
|  | Maximum electric DC. resistance at 20oC | /km | To be specified |  |
|  | Continuous current capacity at max. operating temperature of 900C and in air of 250C | A | To be specified |  |
|  | Diameter of stranded conductor | mm | To be specified |  |
|  | Overall diameter of cable | mm | To be specified |  |
|  | Maximum mass of conductor | kg/km | To be specified |  |
|  | Requirements for testing (according to Technical Specification) |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.21 |  |

HV Connector

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Ordering number |  | To be specified |  |
|  | Applicable standard |  | IEC 694, NEMA CC1, ASTM B22 (A356.0) or equivalent |  |
|  | Type |  | Aluminium alloy |  |
|  | Slip strength of bolted connnector |  | To be specified |  |
|  | Bolt and screw of connector |  | Galvanized steel |  |
|  | Short-time withstand current |  |  |  |
|  | + 500kV side | kA/1s | 50 |  |
|  | + 220kV side | kA/1s | 50 |  |
|  | + 35kV side | kA/1s | 31.5 |  |
|  | Number holes |  | comply |  |
|  | Tightening force for bolt |  |  |  |
|  | - M10 bolt |  | To be specified |  |
|  | - M12 bolt |  | To be specified |  |
|  | - M14 bolt |  | To be specified |  |
|  | - M16 bolt |  | To be specified |  |
|  | Contact grease: |  | Yes |  |
|  | - Manufacturer/Country of Origin |  | To be specified |  |
|  | - Quantity |  | Conformity with connector |  |
|  | Requirements for testing (according to Technical Specification) |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.21 |  |
|  | Catalogue |  | Yes |  |

Important note: For each type of goods specified in the scope of supply and the detailed technical requirements for each type of goods, the Bidder is required to provide a statistic of the test reports of the equipment as required in BD (attached with offered) is described in the following table

LIST OF TEST REPORTS

| No. | Name of equipment | Manufacture/Country of Origin | Name of Laboratory | Name of Equipment | Name of Test | Dated of test/Nam of code | Standard | Evaluated | Remark |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |
| 1 | CIRCUIT BREAKER |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Dielectric test |  |  |  |  |
|  |  |  |  |  | Measurement of the resistance of the main circuit |  |  |  |  |
|  |  |  |  |  | Temperature-rise tests |  |  |  |  |
|  |  |  |  |  | Short-time withstand current and peak withstand current tests |  |  |  |  |
|  |  |  |  |  | Test circuits for short-circuit making and breaking tests |  |  |  |  |
|  |  |  |  |  | Additional tests on auxiliary and control circuits |  |  |  |  |
|  |  |  |  |  | Mechanical operation tests at ambient temperature (class M1). |  |  |  |  |
|  |  |  |  |  | TRV at T100; T60; T30; T10 and fault type “Terminal fault”, “Short line fault”, “Out of phase |  |  |  |  |
|  |  |  |  |  | … |  |  |  |  |
| 2 | Disconnectors and Earthing Switches |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Dielectric tests |  |  |  |  |
|  |  |  |  |  | Measurement of the resistance of the main circuits |  |  |  |  |
|  |  |  |  |  | Continuous current tests |  |  |  |  |
|  |  |  |  |  | Short-time withstand current and peak withstand current tests |  |  |  |  |
|  |  |  |  |  | Mechanical endurance test |  |  |  |  |
|  |  |  |  |  | … |  |  |  |  |
| 3 | Current transformers |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Short-time current tests |  |  |  |  |
|  |  |  |  |  | Temperature-rise test |  |  |  |  |
|  |  |  |  |  | Impulse voltage withstand test on primary terminals |  |  |  |  |
|  |  |  |  |  | Wet test for outdoor type transformers |  |  |  |  |
|  |  |  |  |  | Tests for accuracy |  |  |  |  |
|  |  |  |  |  | Verification of the degree of protection by enclosures |  |  |  |  |
|  |  |  |  |  | Enclosure tightness test at ambient temperature |  |  |  |  |
|  |  |  |  |  | Radio interference voltage measurement |  |  |  |  |
| 4 | Capacitor Voltage Transformers |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Short – Circuit withstand capability test |  |  |  |  |
|  |  |  |  |  | Temperature-rise test |  |  |  |  |
|  |  |  |  |  | Capacitance and tan measurement at power-frequency. |  |  |  |  |
|  |  |  |  |  | Impulse voltage test on primary terminals |  |  |  |  |
|  |  |  |  |  | Chopped impulse test |  |  |  |  |
|  |  |  |  |  | Test for accuracy |  |  |  |  |
|  |  |  |  |  | Wet test for outdoor type transformers |  |  |  |  |
|  |  |  |  |  | Verification of the degree of protection by enclosures |  |  |  |  |
|  |  |  |  |  | Enclosure tightness test at ambient temperature |  |  |  |  |
| 6 | Surge Arresters |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Insulation withstand tests on the arrester housing |  |  |  |  |
|  |  |  |  |  | Residual voltage test |  |  |  |  |
|  |  |  |  |  | Test to verify long term stability under continuous operating voltage |  |  |  |  |
|  |  |  |  |  | Repetitive charge transfer withstand |  |  |  |  |
|  |  |  |  |  | Heat dissipation behaviour verification of test sample |  |  |  |  |
|  |  |  |  |  | Operating duty test |  |  |  |  |
|  |  |  |  |  | Power-frequency voltage versus time -TOV |  |  |  |  |
|  |  |  |  |  | Arrester disconnector/fault indicator (when fitted) |  |  |  |  |
|  |  |  |  |  | Short-circuit tests |  |  |  |  |
|  |  |  |  |  | Bending moment |  |  |  |  |
|  |  |  |  |  | For Polymer-housed surge arresters: Weather ageing test. |  |  |  |  |
| 7 | Post Insulator |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Dry lightning impulse withstand voltage test |  |  |  |  |
|  |  |  |  |  | Wet switching impulse withstand voltage test |  |  |  |  |
|  |  |  |  |  | Wet power frequency withstand voltage test |  |  |  |  |
|  |  |  |  |  | Mechanical failing load test |  |  |  |  |
| 8 | Insulator |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Verification of the dimensions |  |  |  |  |
|  |  |  |  |  | Dry lighting impulse withstand voltage |  |  |  |  |
|  |  |  |  |  | Wet Power frequency withstand voltage |  |  |  |  |
|  |  |  |  |  | Electromechanical failling load test |  |  |  |  |
|  |  |  |  |  | Mechanical failling load test |  |  |  |  |
|  |  |  |  |  | Thermal-mechanical performance test |  |  |  |  |
|  |  |  |  |  | Residual strength test |  |  |  |  |
|  |  |  |  |  | Impulse voltage puncture test |  |  |  |  |
|  |  |  |  |  | Artificial pollution test |  |  |  |  |
| 8 | Insulator sets |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Corona test |  |  |  |  |
|  |  |  |  |  | Radio interference test |  |  |  |  |
|  |  |  |  |  | Dry lightning impulse withstand voltage test |  |  |  |  |
|  |  |  |  |  | Wet power frequency withstand voltage test, |  |  |  |  |
|  |  |  |  |  | Power arc test |  |  |  |  |
|  |  |  |  |  | Mechanical failing load test |  |  |  |  |
| 9 | Fittings |  |  |  |  |  |  |  |  |
|  | Tension Clamp |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Mechanical tests |  |  |  |  |
|  |  |  |  |  | Heating cycle test |  |  |  |  |
|  | Spacer Clamp |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Clamp slip test |  |  |  |  |
|  |  |  |  |  | Torsional slip test |  |  |  |  |
|  |  |  |  |  | Clamp bolt tightening test |  |  |  |  |
|  |  |  |  |  | Corona voltage and RIV test |  |  |  |  |
|  | Suspension clamp |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Mechanical tests |  |  |  |  |
|  |  |  |  |  | Slip test |  |  |  |  |
|  | Compression joint |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Mechanical tests |  |  |  |  |
|  |  |  |  |  | Heating cycle test |  |  |  |  |
|  | Accessories of string insulator |  |  |  | Mechanical tests |  |  |  |  |
|  |  |  |  |  | ….. |  |  |  |  |
| 10 | Conductor |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Stress-strain curves |  |  |  |  |
|  |  |  |  |  | Breaking strength of conductor |  |  |  |  |
|  |  |  |  |  | Joints in aluminum wires |  |  |  |  |
|  |  |  |  |  | Creep Test |  |  |  |  |
|  |  |  |  |  | …… |  |  |  |  |
| 11 | HV terminals connectors |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Temperature rise test |  |  |  |  |
|  |  |  |  |  | Mechanical tensile test |  |  |  |  |
|  |  |  |  |  | Short circuit test |  |  |  |  |
|  |  |  |  |  | Resistance test |  |  |  |  |
|  |  |  |  |  | Radio Interference Voltage (R.I.V) test |  |  |  |  |
| 12 | Lightning wire |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Testing joints on aluminum alloys |  |  |  |  |
|  |  |  |  |  | Testing stress-strain curve. |  |  |  |  |
|  |  |  |  |  | Testing of breaking force of cable. |  |  |  |  |
|  |  |  |  |  | Creep test |  |  |  |  |
| 13 | Current limiting reactor |  |  |  | As per IEC |  |  |  |  |